## Overview
Updated N-0 Summary Report (Rubric-Tailored)
Purpose | Concise N-0 results workbook for final report use; includes only the most report-relevant outputs.
Scope | Normal-operation (N-0) thermal and voltage screening results before ACCOR-based corrective action.
Data basis | Built from solved N-0 hourly summary, pre-ACCOR thermal violations, pre-ACCOR voltage violations, and prior report workbooks.
Key N-0 Metrics |  |  | Report-Use Guidance
Metric | Value | Unit
Maximum pre-ACCOR loading |  | % | • Use System_Summary for one-page quantitative overview.
Average of hourly maximum loading |  | % | • Use Thermal_Results for the main N-0 congestion discussion.
Maximum simultaneous thermal violations |  | count | • Use Voltage_Results for bus-level voltage behaviour.
Average simultaneous thermal violations |  | count | • Use Critical_Hours_Top50 to justify selected N-1 screening hours.
Maximum simultaneous voltage violations |  | count | • Use Area_Context only as supporting context; area mapping is partial.
Average simultaneous voltage violations |  | count
Number of violated branches |  | branches
Number of violating buses |  | buses
Key Findings to Carry into the Written Report
• The solved N-0 dataset covers 5215 hourly cases distributed across the 2025 study year.
• The highest observed pre-ACCOR thermal loading is 165.01%.
• The most persistent thermal bottleneck is branch 816-817, violated in 5128 solved hours.
• Voltage violations are predominantly high-voltage excursions in the current pre-ACCOR N-0 dataset.
• The top-50 worst N-0 hours are included directly for selected N-1 follow-up studies.
Note: This workbook is intentionally lean. Raw detail sheets are hidden to keep the visible report focused and professor-friendly.

## Raw_Hourly (hidden)
time | solve_mode_pre | max_loading_pre | thermal_viol_pre | voltage_viol_pre | month
2025-01-01 | flat_start_nr | 114.06 | 3 | 537 | 2025-01
2025-01-01 01:00 | flat_start_nr | 118.13 | 4 | 543 | 2025-01
2025-01-01 02:00 | flat_start_nr | 126.69 | 3 | 544 | 2025-01
2025-01-01 03:00 | flat_start_nr | 133.81 | 4 | 559 | 2025-01
2025-01-01 04:00 | flat_start_nr | 128.53 | 3 | 545 | 2025-01
2025-01-01 05:00 | flat_start_nr | 124.45 | 3 | 536 | 2025-01
2025-01-01 06:00 | flat_start_nr | 119.74 | 4 | 538 | 2025-01
2025-01-01 07:00 | flat_start_nr | 118.33 | 5 | 535 | 2025-01
2025-01-01 08:00 | flat_start_nr | 120.57 | 5 | 537 | 2025-01
2025-01-01 09:00 | flat_start_nr | 131.34 | 6 | 550 | 2025-01
2025-01-01 10:00 | flat_start_nr | 129.75 | 6 | 546 | 2025-01
2025-01-01 11:00 | flat_start_nr | 126.59 | 5 | 540 | 2025-01
2025-01-01 12:00 | flat_start_nr | 126 | 5 | 538 | 2025-01
2025-01-01 13:00 | flat_start_nr | 123.52 | 5 | 539 | 2025-01
2025-01-01 14:00 | flat_start_nr | 126.19 | 5 | 535 | 2025-01
2025-01-01 15:00 | flat_start_nr | 118.54 | 5 | 543 | 2025-01
2025-01-01 16:00 | flat_start_nr | 110.96 | 4 | 537 | 2025-01
2025-01-01 17:00 | flat_start_nr | 110.62 | 3 | 536 | 2025-01
2025-01-01 18:00 | flat_start_nr | 110.67 | 4 | 536 | 2025-01
2025-01-01 19:00 | flat_start_nr | 113.92 | 3 | 533 | 2025-01
2025-01-01 20:00 | flat_start_nr | 113.52 | 3 | 534 | 2025-01
2025-01-01 21:00 | flat_start_nr | 113.02 | 3 | 531 | 2025-01
2025-01-01 22:00 | flat_start_nr | 112.6 | 4 | 532 | 2025-01
2025-01-01 23:00 | flat_start_nr | 114 | 3 | 532 | 2025-01
2025-01-02 | flat_start_nr | 114.59 | 3 | 540 | 2025-01
2025-01-02 01:00 | flat_start_nr | 115.4 | 3 | 536 | 2025-01
2025-01-02 02:00 | flat_start_nr | 114.35 | 3 | 531 | 2025-01
2025-01-02 03:00 | flat_start_nr | 113.99 | 3 | 535 | 2025-01
2025-01-02 04:00 | flat_start_nr | 113.98 | 3 | 536 | 2025-01
2025-01-02 05:00 | flat_start_nr | 119.19 | 3 | 545 | 2025-01
2025-01-02 06:00 | flat_start_nr | 110.24 | 3 | 541 | 2025-01
2025-01-02 07:00 | flat_start_nr | 109.69 | 3 | 542 | 2025-01
2025-01-02 08:00 | flat_start_nr | 99.68 | 0 | 552 | 2025-01
2025-01-02 09:00 | flat_start_nr | 111.1 | 1 | 549 | 2025-01
2025-01-02 10:00 | flat_start_nr | 115.05 | 1 | 545 | 2025-01
2025-01-02 11:00 | flat_start_nr | 133.15 | 3 | 545 | 2025-01
2025-01-02 12:00 | flat_start_nr | 133.4 | 3 | 546 | 2025-01
2025-01-02 13:00 | flat_start_nr | 134.72 | 3 | 545 | 2025-01
2025-01-02 14:00 | flat_start_nr | 136.41 | 3 | 544 | 2025-01
2025-01-02 15:00 | flat_start_nr | 133.19 | 3 | 545 | 2025-01
2025-01-02 16:00 | flat_start_nr | 118.22 | 2 | 548 | 2025-01
2025-01-02 17:00 | flat_start_nr | 107.7 | 1 | 545 | 2025-01
2025-01-02 18:00 | flat_start_nr | 114.21 | 1 | 544 | 2025-01
2025-01-02 19:00 | flat_start_nr | 121.06 | 2 | 548 | 2025-01
2025-01-02 20:00 | flat_start_nr | 122.83 | 2 | 548 | 2025-01
2025-01-02 21:00 | flat_start_nr | 110.89 | 2 | 544 | 2025-01
2025-01-02 22:00 | flat_start_nr | 113.97 | 4 | 535 | 2025-01
2025-01-02 23:00 | flat_start_nr | 113.75 | 3 | 534 | 2025-01
2025-01-03 | flat_start_nr | 114.65 | 3 | 534 | 2025-01
2025-01-03 01:00 | flat_start_nr | 113.76 | 3 | 534 | 2025-01
2025-01-03 02:00 | flat_start_nr | 113.54 | 3 | 536 | 2025-01
2025-01-03 03:00 | flat_start_nr | 113.41 | 3 | 534 | 2025-01
2025-01-03 04:00 | flat_start_nr | 114.11 | 3 | 533 | 2025-01
2025-01-03 05:00 | flat_start_nr | 113.37 | 3 | 536 | 2025-01
2025-01-03 06:00 | flat_start_nr | 110.08 | 3 | 537 | 2025-01
2025-01-03 07:00 | flat_start_nr | 109.44 | 3 | 535 | 2025-01
2025-01-03 08:00 | flat_start_nr | 109.25 | 3 | 532 | 2025-01
2025-01-03 09:00 | flat_start_nr | 108.97 | 4 | 536 | 2025-01
2025-01-03 10:00 | flat_start_nr | 112.76 | 4 | 535 | 2025-01
2025-01-03 11:00 | flat_start_nr | 117.76 | 5 | 535 | 2025-01
2025-01-03 12:00 | flat_start_nr | 123.3 | 5 | 534 | 2025-01
2025-01-03 13:00 | flat_start_nr | 131.23 | 5 | 540 | 2025-01
2025-01-03 14:00 | flat_start_nr | 134.04 | 5 | 553 | 2025-01
2025-01-03 15:00 | flat_start_nr | 126.44 | 4 | 546 | 2025-01
2025-01-03 16:00 | flat_start_nr | 113.76 | 4 | 537 | 2025-01
2025-01-03 17:00 | flat_start_nr | 113.3 | 4 | 532 | 2025-01
2025-01-03 18:00 | flat_start_nr | 113.34 | 4 | 535 | 2025-01
2025-01-03 19:00 | flat_start_nr | 113.6 | 3 | 536 | 2025-01
2025-01-03 20:00 | flat_start_nr | 114.07 | 3 | 541 | 2025-01
2025-01-03 21:00 | flat_start_nr | 115.76 | 3 | 544 | 2025-01
2025-01-03 22:00 | flat_start_nr | 113.97 | 3 | 541 | 2025-01
2025-01-03 23:00 | flat_start_nr | 114.18 | 2 | 531 | 2025-01
2025-01-04 | flat_start_nr | 114.4 | 3 | 535 | 2025-01
2025-01-04 01:00 | flat_start_nr | 114.08 | 3 | 528 | 2025-01
2025-01-04 02:00 | flat_start_nr | 114.51 | 4 | 545 | 2025-01
2025-01-04 03:00 | flat_start_nr | 114.81 | 4 | 544 | 2025-01
2025-01-04 04:00 | flat_start_nr | 114.72 | 4 | 539 | 2025-01
2025-01-04 05:00 | flat_start_nr | 114.61 | 4 | 538 | 2025-01
2025-01-04 06:00 | flat_start_nr | 114.56 | 3 | 530 | 2025-01
2025-01-04 07:00 | flat_start_nr | 113.65 | 4 | 532 | 2025-01
2025-01-04 08:00 | flat_start_nr | 113.97 | 3 | 531 | 2025-01
2025-01-04 09:00 | flat_start_nr | 116.97 | 5 | 542 | 2025-01
2025-01-04 10:00 | flat_start_nr | 122.82 | 5 | 530 | 2025-01
2025-01-04 11:00 | flat_start_nr | 119.75 | 5 | 528 | 2025-01
2025-01-04 12:00 | flat_start_nr | 118.48 | 5 | 530 | 2025-01
2025-01-04 13:00 | flat_start_nr | 120.09 | 5 | 530 | 2025-01
2025-01-04 14:00 | flat_start_nr | 120.82 | 5 | 530 | 2025-01
2025-01-04 15:00 | flat_start_nr | 128.61 | 4 | 539 | 2025-01
2025-01-04 16:00 | flat_start_nr | 115.66 | 3 | 538 | 2025-01
2025-01-04 17:00 | flat_start_nr | 113.38 | 4 | 534 | 2025-01
2025-01-04 18:00 | flat_start_nr | 113.95 | 5 | 533 | 2025-01
2025-01-04 19:00 | flat_start_nr | 115.7 | 5 | 530 | 2025-01
2025-01-04 20:00 | flat_start_nr | 113.43 | 4 | 538 | 2025-01
2025-01-04 21:00 | flat_start_nr | 113.4 | 4 | 532 | 2025-01
2025-01-04 22:00 | flat_start_nr | 113.4 | 4 | 533 | 2025-01
2025-01-04 23:00 | flat_start_nr | 114.93 | 3 | 544 | 2025-01
2025-01-05 | flat_start_nr | 114.61 | 2 | 539 | 2025-01
2025-01-05 01:00 | flat_start_nr | 114.06 | 3 | 535 | 2025-01
2025-01-05 02:00 | flat_start_nr | 114.36 | 4 | 531 | 2025-01
2025-01-05 03:00 | flat_start_nr | 114.37 | 3 | 534 | 2025-01
2025-01-05 04:00 | flat_start_nr | 114.38 | 3 | 534 | 2025-01
2025-01-05 05:00 | flat_start_nr | 114.24 | 3 | 534 | 2025-01
2025-01-05 06:00 | flat_start_nr | 114.26 | 3 | 538 | 2025-01
2025-01-05 07:00 | flat_start_nr | 113.61 | 3 | 533 | 2025-01
2025-01-05 08:00 | flat_start_nr | 113.78 | 3 | 529 | 2025-01
2025-01-05 09:00 | flat_start_nr | 113.94 | 4 | 521 | 2025-01
2025-01-05 10:00 | flat_start_nr | 113.82 | 4 | 533 | 2025-01
2025-01-05 11:00 | flat_start_nr | 113.58 | 4 | 527 | 2025-01
2025-01-05 12:00 | flat_start_nr | 113.69 | 4 | 528 | 2025-01
2025-01-05 13:00 | flat_start_nr | 113.54 | 4 | 527 | 2025-01
2025-01-05 14:00 | flat_start_nr | 113.12 | 4 | 528 | 2025-01
2025-01-05 15:00 | flat_start_nr | 124.83 | 2 | 539 | 2025-01
2025-01-05 16:00 | flat_start_nr | 119.47 | 2 | 540 | 2025-01
2025-01-05 17:00 | flat_start_nr | 111 | 1 | 542 | 2025-01
2025-01-05 18:00 | flat_start_nr | 109.18 | 1 | 537 | 2025-01
2025-01-05 19:00 | flat_start_nr | 110.52 | 1 | 540 | 2025-01
2025-01-05 20:00 | flat_start_nr | 104.47 | 2 | 528 | 2025-01
2025-01-05 21:00 | flat_start_nr | 109.99 | 3 | 525 | 2025-01
2025-01-05 22:00 | flat_start_nr | 113.2 | 3 | 526 | 2025-01
2025-01-05 23:00 | flat_start_nr | 114.17 | 3 | 534 | 2025-01
2025-01-06 | flat_start_nr | 114.03 | 3 | 530 | 2025-01
2025-01-06 01:00 | flat_start_nr | 114.13 | 3 | 534 | 2025-01
2025-01-06 02:00 | flat_start_nr | 114.16 | 3 | 534 | 2025-01
2025-01-06 03:00 | flat_start_nr | 114.52 | 3 | 534 | 2025-01
2025-01-06 04:00 | flat_start_nr | 114.53 | 3 | 530 | 2025-01
2025-01-06 05:00 | flat_start_nr | 114.15 | 3 | 531 | 2025-01
2025-01-06 06:00 | flat_start_nr | 109.62 | 4 | 531 | 2025-01
2025-01-06 07:00 | flat_start_nr | 107.21 | 1 | 543 | 2025-01
2025-01-06 08:00 | flat_start_nr | 111.05 | 1 | 536 | 2025-01
2025-01-06 09:00 | flat_start_nr | 123.53 | 2 | 538 | 2025-01
2025-01-06 10:00 | flat_start_nr | 111.57 | 3 | 526 | 2025-01
2025-01-06 11:00 | flat_start_nr | 110.3 | 4 | 528 | 2025-01
2025-01-06 12:00 | flat_start_nr | 113.13 | 4 | 524 | 2025-01
2025-01-06 13:00 | flat_start_nr | 111.34 | 4 | 529 | 2025-01
2025-01-06 14:00 | flat_start_nr | 113.69 | 4 | 527 | 2025-01
2025-01-06 15:00 | flat_start_nr | 112.08 | 4 | 525 | 2025-01
2025-01-06 16:00 | flat_start_nr | 114.49 | 1 | 546 | 2025-01
2025-01-06 17:00 | flat_start_nr | 111.62 | 1 | 545 | 2025-01
2025-01-06 18:00 | flat_start_nr | 105.79 | 3 | 535 | 2025-01
2025-01-06 19:00 | flat_start_nr | 108.93 | 4 | 532 | 2025-01
2025-01-06 20:00 | flat_start_nr | 109.1 | 3 | 523 | 2025-01
2025-01-06 21:00 | flat_start_nr | 109.17 | 4 | 527 | 2025-01
2025-01-06 22:00 | flat_start_nr | 112.8 | 4 | 533 | 2025-01
2025-01-06 23:00 | flat_start_nr | 118.62 | 4 | 535 | 2025-01
2025-01-07 | flat_start_nr | 123.05 | 4 | 532 | 2025-01
2025-01-07 01:00 | flat_start_nr | 114.1 | 3 | 535 | 2025-01
2025-01-07 02:00 | flat_start_nr | 115.12 | 3 | 537 | 2025-01
2025-01-07 03:00 | flat_start_nr | 117.09 | 4 | 536 | 2025-01
2025-01-07 04:00 | flat_start_nr | 117.4 | 4 | 537 | 2025-01
2025-01-07 05:00 | flat_start_nr | 127.5 | 3 | 554 | 2025-01
2025-01-07 06:00 | flat_start_nr | 123.08 | 3 | 553 | 2025-01
2025-01-07 07:00 | flat_start_nr | 124.43 | 4 | 568 | 2025-01
2025-01-07 08:00 | flat_start_nr | 119.04 | 4 | 547 | 2025-01
2025-01-07 09:00 | flat_start_nr | 134.38 | 5 | 564 | 2025-01
2025-01-07 10:00 | flat_start_nr | 137.77 | 5 | 566 | 2025-01
2025-01-07 11:00 | flat_start_nr | 153.33 | 8 | 560 | 2025-01
2025-01-07 12:00 | flat_start_nr | 147.7 | 7 | 552 | 2025-01
2025-01-07 13:00 | flat_start_nr | 156.96 | 6 | 568 | 2025-01
2025-01-07 16:00 | flat_start_nr | 151.71 | 7 | 555 | 2025-01
2025-01-07 17:00 | flat_start_nr | 130.71 | 6 | 570 | 2025-01
2025-01-07 18:00 | flat_start_nr | 134.53 | 6 | 572 | 2025-01
2025-01-07 19:00 | flat_start_nr | 135.98 | 5 | 572 | 2025-01
2025-01-07 20:00 | flat_start_nr | 133.4 | 5 | 572 | 2025-01
2025-01-07 21:00 | flat_start_nr | 139.97 | 5 | 571 | 2025-01
2025-01-07 22:00 | flat_start_nr | 155.3 | 7 | 550 | 2025-01
2025-01-07 23:00 | flat_start_nr | 156.73 | 7 | 572 | 2025-01
2025-01-08 06:00 | flat_start_nr | 157.94 | 7 | 569 | 2025-01
2025-01-08 07:00 | flat_start_nr | 152.6 | 6 | 559 | 2025-01
2025-01-08 08:00 | flat_start_nr | 146.33 | 6 | 562 | 2025-01
2025-01-08 09:00 | flat_start_nr | 153.27 | 7 | 555 | 2025-01
2025-01-08 10:00 | flat_start_nr | 151.53 | 6 | 563 | 2025-01
2025-01-08 15:00 | flat_start_nr | 154.75 | 6 | 561 | 2025-01
2025-01-08 16:00 | flat_start_nr | 137.38 | 5 | 570 | 2025-01
2025-01-08 17:00 | flat_start_nr | 124.53 | 4 | 577 | 2025-01
2025-01-08 18:00 | flat_start_nr | 129.56 | 5 | 579 | 2025-01
2025-01-08 19:00 | flat_start_nr | 122.5 | 4 | 581 | 2025-01
2025-01-08 20:00 | flat_start_nr | 124.65 | 5 | 582 | 2025-01
2025-01-08 21:00 | flat_start_nr | 126.64 | 5 | 577 | 2025-01
2025-01-08 22:00 | flat_start_nr | 124.3 | 4 | 575 | 2025-01
2025-01-08 23:00 | flat_start_nr | 123.21 | 4 | 577 | 2025-01
2025-01-09 | flat_start_nr | 133.84 | 5 | 573 | 2025-01
2025-01-09 01:00 | flat_start_nr | 137.82 | 5 | 566 | 2025-01
2025-01-09 02:00 | flat_start_nr | 141.74 | 5 | 569 | 2025-01
2025-01-09 03:00 | flat_start_nr | 154.67 | 7 | 552 | 2025-01
2025-01-09 04:00 | normal_nr | 161.94 | 7 | 567 | 2025-01
2025-01-09 06:00 | flat_start_nr | 157.89 | 6 | 580 | 2025-01
2025-01-09 17:00 | flat_start_nr | 155.35 | 5 | 587 | 2025-01
2025-01-09 18:00 | flat_start_nr | 151.01 | 5 | 555 | 2025-01
2025-01-09 20:00 | flat_start_nr | 146.97 | 5 | 561 | 2025-01
2025-01-09 23:00 | normal_nr | 161.59 | 7 | 574 | 2025-01
2025-01-10 02:00 | flat_start_nr | 159.57 | 7 | 557 | 2025-01
2025-01-10 03:00 | flat_start_nr | 144.97 | 5 | 558 | 2025-01
2025-01-10 04:00 | flat_start_nr | 145.28 | 6 | 557 | 2025-01
2025-01-10 05:00 | flat_start_nr | 142.44 | 5 | 562 | 2025-01
2025-01-10 06:00 | flat_start_nr | 138.44 | 5 | 569 | 2025-01
2025-01-10 07:00 | flat_start_nr | 137.63 | 6 | 569 | 2025-01
2025-01-10 08:00 | flat_start_nr | 137.08 | 6 | 568 | 2025-01
2025-01-10 09:00 | flat_start_nr | 142.12 | 6 | 560 | 2025-01
2025-01-10 10:00 | flat_start_nr | 153.86 | 7 | 545 | 2025-01
2025-01-10 11:00 | flat_start_nr | 152.48 | 7 | 545 | 2025-01
2025-01-10 12:00 | flat_start_nr | 153.59 | 6 | 547 | 2025-01
2025-01-10 13:00 | flat_start_nr | 150.6 | 6 | 560 | 2025-01
2025-01-10 14:00 | flat_start_nr | 147.5 | 6 | 555 | 2025-01
2025-01-10 15:00 | flat_start_nr | 149.84 | 6 | 557 | 2025-01
2025-01-10 16:00 | flat_start_nr | 138.98 | 6 | 578 | 2025-01
2025-01-10 17:00 | flat_start_nr | 120.05 | 5 | 575 | 2025-01
2025-01-10 18:00 | flat_start_nr | 125.81 | 4 | 571 | 2025-01
2025-01-10 19:00 | flat_start_nr | 114.71 | 4 | 572 | 2025-01
2025-01-10 20:00 | flat_start_nr | 125.26 | 5 | 570 | 2025-01
2025-01-10 21:00 | flat_start_nr | 135.91 | 5 | 568 | 2025-01
2025-01-10 22:00 | flat_start_nr | 135.85 | 5 | 568 | 2025-01
2025-01-10 23:00 | flat_start_nr | 137.23 | 5 | 566 | 2025-01
2025-01-11 | flat_start_nr | 139.94 | 5 | 559 | 2025-01
2025-01-11 01:00 | flat_start_nr | 140.28 | 5 | 559 | 2025-01
2025-01-11 02:00 | flat_start_nr | 140.32 | 5 | 559 | 2025-01
2025-01-11 03:00 | flat_start_nr | 140.43 | 5 | 557 | 2025-01
2025-01-11 04:00 | flat_start_nr | 140.85 | 5 | 556 | 2025-01
2025-01-11 05:00 | flat_start_nr | 139.21 | 6 | 558 | 2025-01
2025-01-11 06:00 | flat_start_nr | 137.57 | 5 | 558 | 2025-01
2025-01-11 07:00 | flat_start_nr | 135.92 | 6 | 560 | 2025-01
2025-01-11 08:00 | flat_start_nr | 138.5 | 5 | 558 | 2025-01
2025-01-11 09:00 | flat_start_nr | 149.11 | 5 | 561 | 2025-01
2025-01-11 10:00 | flat_start_nr | 144.64 | 4 | 570 | 2025-01
2025-01-11 11:00 | flat_start_nr | 145.59 | 5 | 567 | 2025-01
2025-01-11 12:00 | flat_start_nr | 141.22 | 5 | 570 | 2025-01
2025-01-11 13:00 | flat_start_nr | 139.08 | 5 | 562 | 2025-01
2025-01-11 14:00 | flat_start_nr | 139.54 | 5 | 561 | 2025-01
2025-01-11 15:00 | flat_start_nr | 131.26 | 5 | 566 | 2025-01
2025-01-11 16:00 | flat_start_nr | 120.67 | 5 | 552 | 2025-01
2025-01-11 17:00 | flat_start_nr | 114.34 | 2 | 551 | 2025-01
2025-01-11 18:00 | flat_start_nr | 114.04 | 3 | 550 | 2025-01
2025-01-11 19:00 | flat_start_nr | 114.96 | 3 | 560 | 2025-01
2025-01-11 20:00 | flat_start_nr | 114.85 | 3 | 565 | 2025-01
2025-01-11 21:00 | flat_start_nr | 114.89 | 2 | 560 | 2025-01
2025-01-11 22:00 | flat_start_nr | 115.75 | 3 | 580 | 2025-01
2025-01-11 23:00 | flat_start_nr | 123.5 | 3 | 574 | 2025-01
2025-01-12 | flat_start_nr | 138.02 | 5 | 570 | 2025-01
2025-01-12 01:00 | flat_start_nr | 121.91 | 4 | 561 | 2025-01
2025-01-12 02:00 | flat_start_nr | 115.15 | 2 | 544 | 2025-01
2025-01-12 03:00 | flat_start_nr | 114.88 | 2 | 547 | 2025-01
2025-01-12 04:00 | flat_start_nr | 114.33 | 3 | 561 | 2025-01
2025-01-12 05:00 | flat_start_nr | 114.91 | 3 | 563 | 2025-01
2025-01-12 06:00 | flat_start_nr | 114.95 | 3 | 563 | 2025-01
2025-01-12 07:00 | flat_start_nr | 114.81 | 2 | 567 | 2025-01
2025-01-12 08:00 | flat_start_nr | 112.3 | 1 | 582 | 2025-01
2025-01-12 09:00 | flat_start_nr | 129.96 | 3 | 578 | 2025-01
2025-01-12 10:00 | flat_start_nr | 131.88 | 5 | 570 | 2025-01
2025-01-12 11:00 | flat_start_nr | 144.81 | 5 | 558 | 2025-01
2025-01-12 12:00 | flat_start_nr | 139.69 | 5 | 571 | 2025-01
2025-01-12 13:00 | flat_start_nr | 142.69 | 5 | 583 | 2025-01
2025-01-12 14:00 | flat_start_nr | 150.05 | 7 | 538 | 2025-01
2025-01-12 15:00 | flat_start_nr | 149.92 | 5 | 535 | 2025-01
2025-01-12 16:00 | flat_start_nr | 135.9 | 5 | 555 | 2025-01
2025-01-12 17:00 | flat_start_nr | 119.33 | 4 | 568 | 2025-01
2025-01-12 18:00 | flat_start_nr | 123.2 | 4 | 569 | 2025-01
2025-01-12 19:00 | flat_start_nr | 137.84 | 5 | 570 | 2025-01
2025-01-12 20:00 | flat_start_nr | 141.57 | 5 | 577 | 2025-01
2025-01-12 21:00 | flat_start_nr | 143.62 | 5 | 570 | 2025-01
2025-01-12 22:00 | flat_start_nr | 150.67 | 6 | 564 | 2025-01
2025-01-12 23:00 | flat_start_nr | 150.14 | 5 | 562 | 2025-01
2025-01-13 | flat_start_nr | 144.39 | 4 | 564 | 2025-01
2025-01-13 01:00 | flat_start_nr | 143.51 | 5 | 561 | 2025-01
2025-01-13 02:00 | flat_start_nr | 142.08 | 5 | 559 | 2025-01
2025-01-13 03:00 | flat_start_nr | 144.1 | 4 | 556 | 2025-01
2025-01-13 04:00 | flat_start_nr | 142.11 | 5 | 560 | 2025-01
2025-01-13 05:00 | flat_start_nr | 140.66 | 5 | 562 | 2025-01
2025-01-13 06:00 | flat_start_nr | 138.57 | 4 | 570 | 2025-01
2025-01-13 07:00 | flat_start_nr | 142.74 | 5 | 565 | 2025-01
2025-01-13 09:00 | flat_start_nr | 141.01 | 5 | 561 | 2025-01
2025-01-13 10:00 | flat_start_nr | 150.52 | 7 | 542 | 2025-01
2025-01-13 12:00 | flat_start_nr | 150.23 | 7 | 539 | 2025-01
2025-01-13 13:00 | flat_start_nr | 146.05 | 5 | 538 | 2025-01
2025-01-13 15:00 | flat_start_nr | 151.74 | 6 | 546 | 2025-01
2025-01-13 16:00 | flat_start_nr | 144.72 | 5 | 554 | 2025-01
2025-01-13 17:00 | flat_start_nr | 135.32 | 4 | 558 | 2025-01
2025-01-13 18:00 | flat_start_nr | 129.38 | 4 | 560 | 2025-01
2025-01-13 19:00 | flat_start_nr | 131.06 | 5 | 563 | 2025-01
2025-01-13 20:00 | flat_start_nr | 128.14 | 4 | 560 | 2025-01
2025-01-13 21:00 | flat_start_nr | 132.35 | 5 | 560 | 2025-01
2025-01-13 22:00 | flat_start_nr | 135.73 | 5 | 562 | 2025-01
2025-01-13 23:00 | flat_start_nr | 127.86 | 4 | 563 | 2025-01
2025-01-14 | flat_start_nr | 133.23 | 5 | 562 | 2025-01
2025-01-14 01:00 | flat_start_nr | 135.88 | 4 | 567 | 2025-01
2025-01-14 02:00 | flat_start_nr | 136.38 | 4 | 561 | 2025-01
2025-01-14 03:00 | flat_start_nr | 135.32 | 4 | 559 | 2025-01
2025-01-14 04:00 | flat_start_nr | 132.54 | 5 | 557 | 2025-01
2025-01-14 05:00 | flat_start_nr | 136.48 | 5 | 556 | 2025-01
2025-01-14 06:00 | flat_start_nr | 133.01 | 5 | 560 | 2025-01
2025-01-14 07:00 | flat_start_nr | 118.45 | 4 | 545 | 2025-01
2025-01-14 08:00 | flat_start_nr | 113.93 | 4 | 535 | 2025-01
2025-01-14 09:00 | flat_start_nr | 116.69 | 4 | 540 | 2025-01
2025-01-14 10:00 | flat_start_nr | 140.79 | 5 | 564 | 2025-01
2025-01-14 11:00 | flat_start_nr | 150.53 | 6 | 549 | 2025-01
2025-01-14 12:00 | flat_start_nr | 138.87 | 5 | 565 | 2025-01
2025-01-14 13:00 | flat_start_nr | 145.66 | 6 | 564 | 2025-01
2025-01-14 14:00 | flat_start_nr | 147.03 | 6 | 561 | 2025-01
2025-01-14 15:00 | flat_start_nr | 149.71 | 5 | 547 | 2025-01
2025-01-14 16:00 | flat_start_nr | 146.69 | 6 | 554 | 2025-01
2025-01-14 17:00 | flat_start_nr | 124.86 | 5 | 566 | 2025-01
2025-01-14 18:00 | flat_start_nr | 127.58 | 5 | 567 | 2025-01
2025-01-14 19:00 | flat_start_nr | 126.37 | 5 | 574 | 2025-01
2025-01-14 20:00 | flat_start_nr | 131.78 | 5 | 563 | 2025-01
2025-01-14 21:00 | flat_start_nr | 135.07 | 5 | 566 | 2025-01
2025-01-14 22:00 | flat_start_nr | 137.16 | 5 | 560 | 2025-01
2025-01-14 23:00 | flat_start_nr | 139 | 5 | 554 | 2025-01
2025-01-15 | flat_start_nr | 140.03 | 5 | 553 | 2025-01
2025-01-15 01:00 | flat_start_nr | 140.79 | 5 | 554 | 2025-01
2025-01-15 02:00 | flat_start_nr | 143.23 | 4 | 564 | 2025-01
2025-01-15 03:00 | flat_start_nr | 143.56 | 4 | 570 | 2025-01
2025-01-15 04:00 | flat_start_nr | 142.8 | 5 | 584 | 2025-01
2025-01-15 05:00 | flat_start_nr | 139.26 | 5 | 564 | 2025-01
2025-01-15 06:00 | flat_start_nr | 130.85 | 5 | 556 | 2025-01
2025-01-15 07:00 | flat_start_nr | 135.69 | 5 | 566 | 2025-01
2025-01-15 16:00 | flat_start_nr | 146.39 | 6 | 556 | 2025-01
2025-01-15 17:00 | flat_start_nr | 128.92 | 2 | 572 | 2025-01
2025-01-15 18:00 | flat_start_nr | 132.85 | 3 | 559 | 2025-01
2025-01-15 19:00 | flat_start_nr | 136.44 | 4 | 555 | 2025-01
2025-01-15 20:00 | flat_start_nr | 146.15 | 5 | 564 | 2025-01
2025-01-15 21:00 | flat_start_nr | 155.83 | 6 | 541 | 2025-01
2025-01-15 22:00 | flat_start_nr | 155.39 | 7 | 537 | 2025-01
2025-01-15 23:00 | flat_start_nr | 148.36 | 6 | 554 | 2025-01
2025-01-16 | flat_start_nr | 151.94 | 6 | 551 | 2025-01
2025-01-16 01:00 | flat_start_nr | 152.28 | 5 | 552 | 2025-01
2025-01-16 02:00 | flat_start_nr | 152.05 | 6 | 551 | 2025-01
2025-01-16 03:00 | flat_start_nr | 152.1 | 6 | 551 | 2025-01
2025-01-16 04:00 | flat_start_nr | 156.87 | 6 | 537 | 2025-01
2025-01-16 05:00 | flat_start_nr | 154.78 | 6 | 539 | 2025-01
2025-01-16 06:00 | flat_start_nr | 152.39 | 5 | 548 | 2025-01
2025-01-16 07:00 | flat_start_nr | 144.74 | 4 | 568 | 2025-01
2025-01-16 08:00 | flat_start_nr | 157.09 | 7 | 557 | 2025-01
2025-01-16 11:00 | flat_start_nr | 154.73 | 6 | 537 | 2025-01
2025-01-16 15:00 | flat_start_nr | 150.25 | 4 | 559 | 2025-01
2025-01-16 16:00 | flat_start_nr | 139.97 | 4 | 574 | 2025-01
2025-01-16 17:00 | flat_start_nr | 120.91 | 4 | 563 | 2025-01
2025-01-16 18:00 | flat_start_nr | 122.66 | 4 | 565 | 2025-01
2025-01-16 19:00 | flat_start_nr | 113.71 | 3 | 554 | 2025-01
2025-01-16 20:00 | flat_start_nr | 113.48 | 3 | 548 | 2025-01
2025-01-16 21:00 | flat_start_nr | 119.76 | 5 | 556 | 2025-01
2025-01-16 22:00 | flat_start_nr | 138.68 | 5 | 557 | 2025-01
2025-01-16 23:00 | flat_start_nr | 132.03 | 3 | 567 | 2025-01
2025-01-17 | flat_start_nr | 135.22 | 4 | 566 | 2025-01
2025-01-17 01:00 | flat_start_nr | 153.24 | 6 | 557 | 2025-01
2025-01-17 02:00 | flat_start_nr | 154.22 | 6 | 546 | 2025-01
2025-01-17 03:00 | flat_start_nr | 155.07 | 6 | 548 | 2025-01
2025-01-17 04:00 | flat_start_nr | 153.53 | 6 | 552 | 2025-01
2025-01-17 05:00 | flat_start_nr | 156.48 | 6 | 544 | 2025-01
2025-01-17 06:00 | flat_start_nr | 143.23 | 4 | 572 | 2025-01
2025-01-17 07:00 | flat_start_nr | 131.7 | 4 | 560 | 2025-01
2025-01-17 08:00 | flat_start_nr | 141.14 | 5 | 555 | 2025-01
2025-01-17 09:00 | flat_start_nr | 124.73 | 5 | 545 | 2025-01
2025-01-17 10:00 | flat_start_nr | 129.98 | 5 | 554 | 2025-01
2025-01-17 11:00 | flat_start_nr | 131.99 | 5 | 552 | 2025-01
2025-01-17 12:00 | flat_start_nr | 135.45 | 5 | 562 | 2025-01
2025-01-17 13:00 | flat_start_nr | 135.95 | 5 | 560 | 2025-01
2025-01-17 14:00 | flat_start_nr | 130.12 | 5 | 544 | 2025-01
2025-01-17 15:00 | flat_start_nr | 123.57 | 4 | 535 | 2025-01
2025-01-17 16:00 | flat_start_nr | 127.77 | 2 | 547 | 2025-01
2025-01-17 17:00 | flat_start_nr | 117.26 | 2 | 558 | 2025-01
2025-01-17 18:00 | flat_start_nr | 119 | 2 | 556 | 2025-01
2025-01-17 19:00 | flat_start_nr | 108.44 | 2 | 544 | 2025-01
2025-01-17 20:00 | flat_start_nr | 113.16 | 2 | 541 | 2025-01
2025-01-17 21:00 | flat_start_nr | 113.15 | 2 | 544 | 2025-01
2025-01-17 22:00 | flat_start_nr | 112.71 | 3 | 544 | 2025-01
2025-01-17 23:00 | flat_start_nr | 114.22 | 3 | 546 | 2025-01
2025-01-18 | flat_start_nr | 114.86 | 3 | 549 | 2025-01
2025-01-18 01:00 | flat_start_nr | 128.5 | 3 | 555 | 2025-01
2025-01-18 02:00 | flat_start_nr | 139.42 | 4 | 565 | 2025-01
2025-01-18 04:00 | flat_start_nr | 151.48 | 5 | 562 | 2025-01
2025-01-18 05:00 | flat_start_nr | 123.16 | 4 | 560 | 2025-01
2025-01-18 06:00 | flat_start_nr | 119.34 | 3 | 553 | 2025-01
2025-01-18 07:00 | flat_start_nr | 126.19 | 3 | 556 | 2025-01
2025-01-18 08:00 | flat_start_nr | 137.1 | 4 | 558 | 2025-01
2025-01-18 09:00 | flat_start_nr | 123.02 | 3 | 545 | 2025-01
2025-01-18 10:00 | flat_start_nr | 112.96 | 2 | 538 | 2025-01
2025-01-18 11:00 | flat_start_nr | 115.57 | 2 | 538 | 2025-01
2025-01-18 12:00 | flat_start_nr | 126.95 | 3 | 523 | 2025-01
2025-01-18 13:00 | flat_start_nr | 136.53 | 5 | 530 | 2025-01
2025-01-18 14:00 | flat_start_nr | 142.14 | 5 | 543 | 2025-01
2025-01-18 15:00 | flat_start_nr | 138.89 | 5 | 538 | 2025-01
2025-01-18 16:00 | flat_start_nr | 131.49 | 5 | 527 | 2025-01
2025-01-18 17:00 | flat_start_nr | 115.34 | 2 | 546 | 2025-01
2025-01-18 18:00 | flat_start_nr | 116.91 | 2 | 546 | 2025-01
2025-01-18 19:00 | flat_start_nr | 130.74 | 3 | 547 | 2025-01
2025-01-18 20:00 | flat_start_nr | 124 | 2 | 548 | 2025-01
2025-01-18 21:00 | flat_start_nr | 116.01 | 2 | 546 | 2025-01
2025-01-18 22:00 | flat_start_nr | 117.25 | 2 | 546 | 2025-01
2025-01-18 23:00 | flat_start_nr | 120.05 | 2 | 545 | 2025-01
2025-01-19 | flat_start_nr | 114.04 | 1 | 545 | 2025-01
2025-01-19 01:00 | flat_start_nr | 112.29 | 1 | 539 | 2025-01
2025-01-19 02:00 | flat_start_nr | 107.41 | 2 | 531 | 2025-01
2025-01-19 03:00 | flat_start_nr | 113.65 | 3 | 535 | 2025-01
2025-01-19 04:00 | flat_start_nr | 113.4 | 3 | 535 | 2025-01
2025-01-19 05:00 | flat_start_nr | 113.54 | 3 | 534 | 2025-01
2025-01-19 06:00 | flat_start_nr | 113.66 | 3 | 533 | 2025-01
2025-01-19 07:00 | flat_start_nr | 113.04 | 3 | 533 | 2025-01
2025-01-19 08:00 | flat_start_nr | 121.97 | 5 | 538 | 2025-01
2025-01-19 09:00 | flat_start_nr | 142.59 | 5 | 522 | 2025-01
2025-01-19 10:00 | flat_start_nr | 150.08 | 7 | 530 | 2025-01
2025-01-19 11:00 | flat_start_nr | 144.45 | 5 | 542 | 2025-01
2025-01-19 12:00 | flat_start_nr | 137.39 | 5 | 548 | 2025-01
2025-01-19 13:00 | flat_start_nr | 136.94 | 5 | 546 | 2025-01
2025-01-19 14:00 | flat_start_nr | 141.64 | 5 | 565 | 2025-01
2025-01-19 15:00 | flat_start_nr | 139.88 | 5 | 560 | 2025-01
2025-01-19 16:00 | flat_start_nr | 139.7 | 5 | 550 | 2025-01
2025-01-19 17:00 | flat_start_nr | 112.08 | 3 | 545 | 2025-01
2025-01-19 18:00 | flat_start_nr | 109.6 | 3 | 540 | 2025-01
2025-01-19 19:00 | flat_start_nr | 109.29 | 3 | 540 | 2025-01
2025-01-19 20:00 | flat_start_nr | 109.04 | 3 | 532 | 2025-01
2025-01-19 21:00 | flat_start_nr | 109.16 | 2 | 534 | 2025-01
2025-01-19 22:00 | flat_start_nr | 112.56 | 2 | 535 | 2025-01
2025-01-19 23:00 | flat_start_nr | 112.1 | 3 | 535 | 2025-01
2025-01-20 | flat_start_nr | 112.66 | 2 | 534 | 2025-01
2025-01-20 01:00 | flat_start_nr | 112.78 | 2 | 536 | 2025-01
2025-01-20 02:00 | flat_start_nr | 112.94 | 2 | 538 | 2025-01
2025-01-20 03:00 | flat_start_nr | 113.01 | 2 | 541 | 2025-01
2025-01-20 04:00 | flat_start_nr | 113.13 | 2 | 533 | 2025-01
2025-01-20 05:00 | flat_start_nr | 112.37 | 4 | 536 | 2025-01
2025-01-20 06:00 | flat_start_nr | 116.28 | 2 | 551 | 2025-01
2025-01-20 07:00 | flat_start_nr | 108.65 | 1 | 550 | 2025-01
2025-01-20 08:00 | flat_start_nr | 143.21 | 3 | 570 | 2025-01
2025-01-20 09:00 | flat_start_nr | 152.28 | 5 | 555 | 2025-01
2025-01-20 11:00 | flat_start_nr | 151.57 | 4 | 537 | 2025-01
2025-01-20 12:00 | flat_start_nr | 133.83 | 3 | 558 | 2025-01
2025-01-20 13:00 | flat_start_nr | 141.52 | 4 | 564 | 2025-01
2025-01-20 14:00 | flat_start_nr | 144.08 | 3 | 568 | 2025-01
2025-01-20 15:00 | flat_start_nr | 138.49 | 4 | 562 | 2025-01
2025-01-20 16:00 | flat_start_nr | 130.63 | 4 | 543 | 2025-01
2025-01-20 17:00 | flat_start_nr | 131.3 | 4 | 549 | 2025-01
2025-01-20 18:00 | flat_start_nr | 126.9 | 4 | 548 | 2025-01
2025-01-20 19:00 | flat_start_nr | 123.86 | 4 | 559 | 2025-01
2025-01-20 20:00 | flat_start_nr | 122.7 | 4 | 552 | 2025-01
2025-01-20 21:00 | flat_start_nr | 136.33 | 4 | 564 | 2025-01
2025-01-20 22:00 | flat_start_nr | 154.91 | 6 | 538 | 2025-01
2025-01-21 | flat_start_nr | 158.9 | 6 | 570 | 2025-01
2025-01-21 02:00 | flat_start_nr | 155.81 | 6 | 549 | 2025-01
2025-01-21 06:00 | flat_start_nr | 139.83 | 4 | 570 | 2025-01
2025-01-21 07:00 | flat_start_nr | 121.11 | 3 | 550 | 2025-01
2025-01-21 08:00 | flat_start_nr | 120.61 | 3 | 542 | 2025-01
2025-01-21 09:00 | flat_start_nr | 140.06 | 3 | 545 | 2025-01
2025-01-21 10:00 | flat_start_nr | 150.93 | 4 | 544 | 2025-01
2025-01-21 11:00 | flat_start_nr | 155.99 | 5 | 568 | 2025-01
2025-01-21 16:00 | flat_start_nr | 145.36 | 6 | 551 | 2025-01
2025-01-21 17:00 | flat_start_nr | 137.51 | 6 | 549 | 2025-01
2025-01-21 18:00 | flat_start_nr | 136.71 | 5 | 555 | 2025-01
2025-01-21 19:00 | flat_start_nr | 136.33 | 4 | 570 | 2025-01
2025-01-21 20:00 | flat_start_nr | 144.99 | 4 | 567 | 2025-01
2025-01-21 21:00 | flat_start_nr | 154.86 | 6 | 543 | 2025-01
2025-01-22 06:00 | flat_start_nr | 157.68 | 6 | 564 | 2025-01
2025-01-22 07:00 | flat_start_nr | 134.36 | 4 | 571 | 2025-01
2025-01-22 08:00 | flat_start_nr | 138.13 | 5 | 553 | 2025-01
2025-01-22 09:00 | flat_start_nr | 132.55 | 5 | 550 | 2025-01
2025-01-22 10:00 | flat_start_nr | 143.01 | 5 | 545 | 2025-01
2025-01-22 11:00 | flat_start_nr | 156.43 | 5 | 559 | 2025-01
2025-01-22 13:00 | flat_start_nr | 155.3 | 5 | 574 | 2025-01
2025-01-22 14:00 | flat_start_nr | 153.39 | 5 | 551 | 2025-01
2025-01-22 16:00 | flat_start_nr | 138.95 | 4 | 553 | 2025-01
2025-01-22 17:00 | flat_start_nr | 133.24 | 4 | 565 | 2025-01
2025-01-22 18:00 | flat_start_nr | 138.36 | 4 | 568 | 2025-01
2025-01-22 19:00 | flat_start_nr | 120.5 | 2 | 548 | 2025-01
2025-01-22 20:00 | flat_start_nr | 105.96 | 3 | 539 | 2025-01
2025-01-22 21:00 | flat_start_nr | 113.31 | 3 | 536 | 2025-01
2025-01-22 22:00 | flat_start_nr | 113.54 | 2 | 534 | 2025-01
2025-01-22 23:00 | flat_start_nr | 113.27 | 3 | 536 | 2025-01
2025-01-23 | flat_start_nr | 122.31 | 4 | 544 | 2025-01
2025-01-23 01:00 | flat_start_nr | 123.84 | 3 | 547 | 2025-01
2025-01-23 02:00 | flat_start_nr | 135.22 | 4 | 562 | 2025-01
2025-01-23 03:00 | flat_start_nr | 156.75 | 5 | 579 | 2025-01
2025-01-23 06:00 | normal_nr | 161.34 | 6 | 568 | 2025-01
2025-01-23 07:00 | flat_start_nr | 142.04 | 4 | 570 | 2025-01
2025-01-23 08:00 | flat_start_nr | 144.15 | 5 | 562 | 2025-01
2025-01-23 09:00 | flat_start_nr | 143.86 | 4 | 560 | 2025-01
2025-01-23 10:00 | flat_start_nr | 140.45 | 4 | 559 | 2025-01
2025-01-23 11:00 | flat_start_nr | 140.33 | 4 | 560 | 2025-01
2025-01-23 12:00 | flat_start_nr | 147.73 | 4 | 547 | 2025-01
2025-01-23 17:00 | flat_start_nr | 134.4 | 5 | 576 | 2025-01
2025-01-23 18:00 | flat_start_nr | 131.5 | 4 | 560 | 2025-01
2025-01-23 19:00 | flat_start_nr | 113.5 | 4 | 548 | 2025-01
2025-01-23 20:00 | flat_start_nr | 114.18 | 3 | 557 | 2025-01
2025-01-23 21:00 | flat_start_nr | 123.58 | 3 | 551 | 2025-01
2025-01-23 22:00 | flat_start_nr | 128.53 | 3 | 564 | 2025-01
2025-01-23 23:00 | flat_start_nr | 140.06 | 4 | 578 | 2025-01
2025-01-24 | flat_start_nr | 144.53 | 4 | 571 | 2025-01
2025-01-24 01:00 | flat_start_nr | 145.81 | 5 | 572 | 2025-01
2025-01-24 02:00 | flat_start_nr | 153.69 | 6 | 552 | 2025-01
2025-01-24 03:00 | flat_start_nr | 153.51 | 6 | 552 | 2025-01
2025-01-24 04:00 | flat_start_nr | 156.2 | 6 | 545 | 2025-01
2025-01-24 06:00 | flat_start_nr | 148.44 | 5 | 559 | 2025-01
2025-01-24 07:00 | flat_start_nr | 130.22 | 4 | 568 | 2025-01
2025-01-24 08:00 | flat_start_nr | 134.8 | 5 | 557 | 2025-01
2025-01-24 09:00 | flat_start_nr | 140.32 | 4 | 555 | 2025-01
2025-01-24 10:00 | flat_start_nr | 148.46 | 4 | 548 | 2025-01
2025-01-24 11:00 | flat_start_nr | 144.2 | 3 | 569 | 2025-01
2025-01-24 12:00 | flat_start_nr | 142.42 | 3 | 565 | 2025-01
2025-01-24 13:00 | flat_start_nr | 138.27 | 4 | 548 | 2025-01
2025-01-24 14:00 | flat_start_nr | 141.67 | 3 | 556 | 2025-01
2025-01-24 15:00 | flat_start_nr | 154.78 | 5 | 568 | 2025-01
2025-01-24 16:00 | flat_start_nr | 145.12 | 3 | 564 | 2025-01
2025-01-24 17:00 | flat_start_nr | 132.06 | 4 | 547 | 2025-01
2025-01-24 18:00 | flat_start_nr | 124.53 | 3 | 548 | 2025-01
2025-01-24 19:00 | flat_start_nr | 116.74 | 4 | 564 | 2025-01
2025-01-24 20:00 | flat_start_nr | 119.32 | 4 | 562 | 2025-01
2025-01-24 21:00 | flat_start_nr | 126.57 | 4 | 561 | 2025-01
2025-01-24 22:00 | flat_start_nr | 119.57 | 4 | 557 | 2025-01
2025-01-24 23:00 | flat_start_nr | 118.78 | 5 | 573 | 2025-01
2025-01-25 | flat_start_nr | 120.88 | 3 | 555 | 2025-01
2025-01-25 01:00 | flat_start_nr | 114.22 | 3 | 552 | 2025-01
2025-01-25 02:00 | flat_start_nr | 116.4 | 4 | 548 | 2025-01
2025-01-25 03:00 | flat_start_nr | 135.45 | 4 | 554 | 2025-01
2025-01-25 05:00 | flat_start_nr | 155.69 | 5 | 582 | 2025-01
2025-01-25 06:00 | flat_start_nr | 148.73 | 4 | 561 | 2025-01
2025-01-25 07:00 | flat_start_nr | 135.98 | 3 | 571 | 2025-01
2025-01-25 08:00 | flat_start_nr | 142.17 | 4 | 554 | 2025-01
2025-01-25 17:00 | flat_start_nr | 133.61 | 4 | 573 | 2025-01
2025-01-25 18:00 | flat_start_nr | 130.53 | 4 | 564 | 2025-01
2025-01-25 19:00 | flat_start_nr | 142.47 | 4 | 572 | 2025-01
2025-01-25 20:00 | flat_start_nr | 156.08 | 6 | 550 | 2025-01
2025-01-25 21:00 | flat_start_nr | 156.48 | 6 | 576 | 2025-01
2025-01-25 22:00 | flat_start_nr | 152.99 | 6 | 561 | 2025-01
2025-01-25 23:00 | flat_start_nr | 148.79 | 5 | 547 | 2025-01
2025-01-26 | flat_start_nr | 135.15 | 4 | 570 | 2025-01
2025-01-26 01:00 | flat_start_nr | 126.93 | 4 | 561 | 2025-01
2025-01-26 02:00 | flat_start_nr | 126.43 | 4 | 554 | 2025-01
2025-01-26 03:00 | flat_start_nr | 123.24 | 3 | 541 | 2025-01
2025-01-26 04:00 | flat_start_nr | 118.2 | 3 | 542 | 2025-01
2025-01-26 05:00 | flat_start_nr | 120.69 | 3 | 551 | 2025-01
2025-01-26 06:00 | flat_start_nr | 120.92 | 3 | 556 | 2025-01
2025-01-26 07:00 | flat_start_nr | 129.32 | 3 | 554 | 2025-01
2025-01-26 08:00 | flat_start_nr | 152.95 | 6 | 547 | 2025-01
2025-01-26 17:00 | flat_start_nr | 140.57 | 4 | 578 | 2025-01
2025-01-26 18:00 | flat_start_nr | 130.3 | 4 | 561 | 2025-01
2025-01-26 19:00 | flat_start_nr | 136.9 | 5 | 564 | 2025-01
2025-01-26 20:00 | flat_start_nr | 147.29 | 5 | 560 | 2025-01
2025-01-26 21:00 | flat_start_nr | 159.6 | 6 | 553 | 2025-01
2025-01-27 06:00 | normal_nr | 162.25 | 6 | 561 | 2025-01
2025-01-27 07:00 | flat_start_nr | 141.4 | 5 | 569 | 2025-01
2025-01-27 17:00 | flat_start_nr | 154.72 | 7 | 578 | 2025-01
2025-01-27 18:00 | flat_start_nr | 141.41 | 5 | 573 | 2025-01
2025-01-27 19:00 | flat_start_nr | 139.08 | 5 | 571 | 2025-01
2025-01-27 20:00 | flat_start_nr | 139.4 | 5 | 567 | 2025-01
2025-01-27 21:00 | flat_start_nr | 146.77 | 6 | 553 | 2025-01
2025-01-28 07:00 | flat_start_nr | 139.13 | 4 | 563 | 2025-01
2025-01-28 08:00 | flat_start_nr | 145.04 | 5 | 559 | 2025-01
2025-01-28 09:00 | flat_start_nr | 142.06 | 5 | 572 | 2025-01
2025-01-28 10:00 | flat_start_nr | 140.01 | 5 | 568 | 2025-01
2025-01-28 17:00 | flat_start_nr | 115.53 | 3 | 535 | 2025-01
2025-01-28 18:00 | flat_start_nr | 114.75 | 3 | 537 | 2025-01
2025-01-28 19:00 | flat_start_nr | 126.99 | 3 | 546 | 2025-01
2025-01-28 20:00 | flat_start_nr | 132.79 | 4 | 542 | 2025-01
2025-01-28 21:00 | flat_start_nr | 135.9 | 4 | 541 | 2025-01
2025-01-28 22:00 | flat_start_nr | 130.13 | 4 | 541 | 2025-01
2025-01-28 23:00 | flat_start_nr | 124.17 | 3 | 541 | 2025-01
2025-01-29 | flat_start_nr | 121.33 | 3 | 546 | 2025-01
2025-01-29 01:00 | flat_start_nr | 130.75 | 4 | 546 | 2025-01
2025-01-29 02:00 | flat_start_nr | 128.8 | 4 | 542 | 2025-01
2025-01-29 03:00 | flat_start_nr | 136.09 | 5 | 553 | 2025-01
2025-01-29 04:00 | flat_start_nr | 138.7 | 4 | 552 | 2025-01
2025-01-29 05:00 | flat_start_nr | 141.11 | 4 | 559 | 2025-01
2025-01-29 06:00 | flat_start_nr | 134.47 | 4 | 558 | 2025-01
2025-01-29 07:00 | flat_start_nr | 133.67 | 5 | 546 | 2025-01
2025-01-29 08:00 | flat_start_nr | 151.84 | 6 | 520 | 2025-01
2025-01-29 09:00 | flat_start_nr | 149.57 | 5 | 524 | 2025-01
2025-01-29 10:00 | flat_start_nr | 146.05 | 5 | 539 | 2025-01
2025-01-29 11:00 | flat_start_nr | 148.12 | 4 | 526 | 2025-01
2025-01-29 12:00 | flat_start_nr | 154.57 | 5 | 564 | 2025-01
2025-01-29 13:00 | flat_start_nr | 154.02 | 5 | 529 | 2025-01
2025-01-29 14:00 | flat_start_nr | 151.72 | 5 | 525 | 2025-01
2025-01-29 15:00 | flat_start_nr | 146.43 | 4 | 544 | 2025-01
2025-01-29 16:00 | flat_start_nr | 141.39 | 4 | 548 | 2025-01
2025-01-29 17:00 | flat_start_nr | 120.72 | 5 | 538 | 2025-01
2025-01-29 18:00 | flat_start_nr | 129.65 | 3 | 536 | 2025-01
2025-01-29 19:00 | flat_start_nr | 128.23 | 4 | 537 | 2025-01
2025-01-29 20:00 | flat_start_nr | 127.06 | 4 | 542 | 2025-01
2025-01-29 21:00 | flat_start_nr | 125.01 | 4 | 543 | 2025-01
2025-01-29 22:00 | flat_start_nr | 128.2 | 4 | 544 | 2025-01
2025-01-29 23:00 | flat_start_nr | 130.99 | 5 | 555 | 2025-01
2025-01-30 | flat_start_nr | 139.68 | 4 | 564 | 2025-01
2025-01-30 01:00 | flat_start_nr | 139.21 | 4 | 565 | 2025-01
2025-01-30 02:00 | flat_start_nr | 143.16 | 4 | 573 | 2025-01
2025-01-30 03:00 | flat_start_nr | 141.8 | 3 | 565 | 2025-01
2025-01-30 04:00 | flat_start_nr | 136.76 | 4 | 558 | 2025-01
2025-01-30 05:00 | flat_start_nr | 133.43 | 4 | 558 | 2025-01
2025-01-30 06:00 | flat_start_nr | 129.53 | 4 | 549 | 2025-01
2025-01-30 07:00 | flat_start_nr | 126.08 | 3 | 547 | 2025-01
2025-01-30 08:00 | flat_start_nr | 150.03 | 7 | 528 | 2025-01
2025-01-30 09:00 | flat_start_nr | 148.77 | 6 | 531 | 2025-01
2025-01-30 10:00 | flat_start_nr | 144.44 | 4 | 534 | 2025-01
2025-01-30 11:00 | flat_start_nr | 143.41 | 4 | 541 | 2025-01
2025-01-30 12:00 | flat_start_nr | 134.6 | 5 | 537 | 2025-01
2025-01-30 13:00 | flat_start_nr | 129.08 | 4 | 536 | 2025-01
2025-01-30 14:00 | flat_start_nr | 121.25 | 4 | 527 | 2025-01
2025-01-30 15:00 | flat_start_nr | 128.33 | 4 | 528 | 2025-01
2025-01-30 16:00 | flat_start_nr | 127.77 | 4 | 534 | 2025-01
2025-01-30 17:00 | flat_start_nr | 113.55 | 3 | 540 | 2025-01
2025-01-30 18:00 | flat_start_nr | 113.6 | 3 | 537 | 2025-01
2025-01-30 19:00 | flat_start_nr | 113.82 | 3 | 538 | 2025-01
2025-01-30 20:00 | flat_start_nr | 113.83 | 3 | 535 | 2025-01
2025-01-30 21:00 | flat_start_nr | 113.92 | 3 | 539 | 2025-01
2025-01-30 22:00 | flat_start_nr | 113.77 | 3 | 540 | 2025-01
2025-01-30 23:00 | flat_start_nr | 114.5 | 2 | 537 | 2025-01
2025-01-31 | flat_start_nr | 114.55 | 2 | 538 | 2025-01
2025-01-31 01:00 | flat_start_nr | 114.58 | 3 | 544 | 2025-01
2025-01-31 02:00 | flat_start_nr | 114.5 | 3 | 543 | 2025-01
2025-01-31 03:00 | flat_start_nr | 114.45 | 3 | 546 | 2025-01
2025-01-31 04:00 | flat_start_nr | 114.06 | 2 | 541 | 2025-01
2025-01-31 05:00 | flat_start_nr | 113.26 | 3 | 541 | 2025-01
2025-01-31 06:00 | flat_start_nr | 113.23 | 2 | 536 | 2025-01
2025-01-31 07:00 | flat_start_nr | 112.9 | 3 | 531 | 2025-01
2025-01-31 08:00 | flat_start_nr | 113.14 | 3 | 527 | 2025-01
2025-01-31 09:00 | flat_start_nr | 114.11 | 3 | 534 | 2025-01
2025-01-31 10:00 | flat_start_nr | 117.58 | 4 | 541 | 2025-01
2025-01-31 11:00 | flat_start_nr | 121.56 | 5 | 543 | 2025-01
2025-01-31 12:00 | flat_start_nr | 128.63 | 4 | 551 | 2025-01
2025-01-31 13:00 | flat_start_nr | 133.14 | 4 | 545 | 2025-01
2025-01-31 14:00 | flat_start_nr | 134.44 | 5 | 557 | 2025-01
2025-01-31 15:00 | flat_start_nr | 131.3 | 5 | 546 | 2025-01
2025-01-31 16:00 | flat_start_nr | 126.56 | 5 | 541 | 2025-01
2025-01-31 17:00 | flat_start_nr | 116.41 | 5 | 540 | 2025-01
2025-01-31 18:00 | flat_start_nr | 113.75 | 3 | 537 | 2025-01
2025-01-31 19:00 | flat_start_nr | 113.74 | 3 | 533 | 2025-01
2025-01-31 20:00 | flat_start_nr | 113.62 | 3 | 531 | 2025-01
2025-01-31 21:00 | flat_start_nr | 113.65 | 3 | 533 | 2025-01
2025-01-31 22:00 | flat_start_nr | 115.55 | 4 | 533 | 2025-01
2025-01-31 23:00 | flat_start_nr | 113.13 | 3 | 532 | 2025-01
2025-02-01 | flat_start_nr | 112.92 | 3 | 540 | 2025-02
2025-02-01 01:00 | flat_start_nr | 112.72 | 3 | 545 | 2025-02
2025-02-01 02:00 | flat_start_nr | 112.6 | 3 | 544 | 2025-02
2025-02-01 03:00 | flat_start_nr | 112.37 | 3 | 548 | 2025-02
2025-02-01 04:00 | flat_start_nr | 112.42 | 3 | 539 | 2025-02
2025-02-01 05:00 | flat_start_nr | 112.12 | 3 | 540 | 2025-02
2025-02-01 06:00 | flat_start_nr | 112.15 | 3 | 537 | 2025-02
2025-02-01 07:00 | flat_start_nr | 112.2 | 2 | 536 | 2025-02
2025-02-01 08:00 | flat_start_nr | 112.2 | 3 | 542 | 2025-02
2025-02-01 09:00 | flat_start_nr | 121.66 | 4 | 537 | 2025-02
2025-02-01 10:00 | flat_start_nr | 129.42 | 5 | 543 | 2025-02
2025-02-01 11:00 | flat_start_nr | 132.33 | 5 | 554 | 2025-02
2025-02-01 12:00 | flat_start_nr | 129.22 | 4 | 543 | 2025-02
2025-02-01 13:00 | flat_start_nr | 124.75 | 5 | 545 | 2025-02
2025-02-01 14:00 | flat_start_nr | 136.93 | 5 | 545 | 2025-02
2025-02-01 15:00 | flat_start_nr | 136.49 | 5 | 547 | 2025-02
2025-02-01 16:00 | flat_start_nr | 131.67 | 5 | 543 | 2025-02
2025-02-01 17:00 | flat_start_nr | 117.88 | 5 | 551 | 2025-02
2025-02-01 18:00 | flat_start_nr | 111.3 | 3 | 553 | 2025-02
2025-02-01 19:00 | flat_start_nr | 114.2 | 3 | 551 | 2025-02
2025-02-01 20:00 | flat_start_nr | 111.91 | 3 | 557 | 2025-02
2025-02-01 21:00 | flat_start_nr | 114.08 | 2 | 555 | 2025-02
2025-02-01 22:00 | flat_start_nr | 119.6 | 3 | 555 | 2025-02
2025-02-01 23:00 | flat_start_nr | 128.92 | 3 | 548 | 2025-02
2025-02-02 | flat_start_nr | 131.01 | 4 | 553 | 2025-02
2025-02-02 01:00 | flat_start_nr | 129.37 | 3 | 556 | 2025-02
2025-02-02 02:00 | flat_start_nr | 123.5 | 4 | 557 | 2025-02
2025-02-02 03:00 | flat_start_nr | 123.43 | 4 | 556 | 2025-02
2025-02-02 04:00 | flat_start_nr | 127.44 | 4 | 557 | 2025-02
2025-02-02 05:00 | flat_start_nr | 132.53 | 5 | 558 | 2025-02
2025-02-02 06:00 | flat_start_nr | 136.47 | 4 | 551 | 2025-02
2025-02-02 07:00 | flat_start_nr | 132.29 | 5 | 552 | 2025-02
2025-02-02 08:00 | flat_start_nr | 132.22 | 5 | 544 | 2025-02
2025-02-02 09:00 | flat_start_nr | 121.04 | 4 | 541 | 2025-02
2025-02-02 10:00 | flat_start_nr | 125.9 | 4 | 533 | 2025-02
2025-02-02 11:00 | flat_start_nr | 128.75 | 4 | 541 | 2025-02
2025-02-02 12:00 | flat_start_nr | 129.37 | 5 | 537 | 2025-02
2025-02-02 13:00 | flat_start_nr | 125.34 | 4 | 537 | 2025-02
2025-02-02 14:00 | flat_start_nr | 131.85 | 5 | 539 | 2025-02
2025-02-02 15:00 | flat_start_nr | 141.42 | 5 | 548 | 2025-02
2025-02-02 16:00 | flat_start_nr | 137.15 | 5 | 544 | 2025-02
2025-02-02 17:00 | flat_start_nr | 117.05 | 5 | 526 | 2025-02
2025-02-02 18:00 | flat_start_nr | 109.48 | 3 | 539 | 2025-02
2025-02-02 19:00 | flat_start_nr | 109.72 | 3 | 536 | 2025-02
2025-02-02 20:00 | flat_start_nr | 116.75 | 5 | 544 | 2025-02
2025-02-02 21:00 | flat_start_nr | 120.52 | 4 | 542 | 2025-02
2025-02-02 22:00 | flat_start_nr | 120.4 | 4 | 544 | 2025-02
2025-02-02 23:00 | flat_start_nr | 120.82 | 5 | 543 | 2025-02
2025-02-03 | flat_start_nr | 121.55 | 5 | 544 | 2025-02
2025-02-03 01:00 | flat_start_nr | 130.01 | 5 | 541 | 2025-02
2025-02-03 02:00 | flat_start_nr | 125.43 | 4 | 542 | 2025-02
2025-02-03 03:00 | flat_start_nr | 118.87 | 3 | 536 | 2025-02
2025-02-03 04:00 | flat_start_nr | 124.74 | 2 | 543 | 2025-02
2025-02-03 05:00 | flat_start_nr | 125.46 | 2 | 541 | 2025-02
2025-02-03 06:00 | flat_start_nr | 135.3 | 3 | 548 | 2025-02
2025-02-03 07:00 | flat_start_nr | 116.5 | 3 | 535 | 2025-02
2025-02-03 08:00 | flat_start_nr | 122.61 | 3 | 532 | 2025-02
2025-02-03 09:00 | flat_start_nr | 126.52 | 3 | 533 | 2025-02
2025-02-03 10:00 | flat_start_nr | 127.82 | 3 | 534 | 2025-02
2025-02-03 11:00 | flat_start_nr | 127.79 | 3 | 533 | 2025-02
2025-02-03 12:00 | flat_start_nr | 126.26 | 3 | 531 | 2025-02
2025-02-03 13:00 | flat_start_nr | 130.91 | 4 | 535 | 2025-02
2025-02-03 14:00 | flat_start_nr | 134.54 | 4 | 529 | 2025-02
2025-02-03 15:00 | flat_start_nr | 133.41 | 4 | 531 | 2025-02
2025-02-03 16:00 | flat_start_nr | 120.38 | 3 | 543 | 2025-02
2025-02-03 17:00 | flat_start_nr | 104.64 | 1 | 548 | 2025-02
2025-02-03 18:00 | flat_start_nr | 104.86 | 1 | 533 | 2025-02
2025-02-03 19:00 | flat_start_nr | 105.4 | 2 | 535 | 2025-02
2025-02-03 20:00 | flat_start_nr | 117.7 | 3 | 537 | 2025-02
2025-02-03 21:00 | flat_start_nr | 133.26 | 3 | 548 | 2025-02
2025-02-03 22:00 | flat_start_nr | 154.29 | 6 | 558 | 2025-02
2025-02-03 23:00 | flat_start_nr | 153.68 | 6 | 532 | 2025-02
2025-02-04 | flat_start_nr | 141.55 | 4 | 553 | 2025-02
2025-02-04 01:00 | flat_start_nr | 144.76 | 4 | 546 | 2025-02
2025-02-04 02:00 | flat_start_nr | 144.83 | 4 | 546 | 2025-02
2025-02-04 06:00 | flat_start_nr | 150.34 | 5 | 504 | 2025-02
2025-02-04 07:00 | flat_start_nr | 142.59 | 3 | 524 | 2025-02
2025-02-04 08:00 | flat_start_nr | 150.43 | 5 | 522 | 2025-02
2025-02-04 09:00 | flat_start_nr | 149.63 | 5 | 524 | 2025-02
2025-02-04 10:00 | flat_start_nr | 142.75 | 4 | 525 | 2025-02
2025-02-04 11:00 | flat_start_nr | 145.31 | 4 | 504 | 2025-02
2025-02-04 12:00 | flat_start_nr | 144.74 | 4 | 505 | 2025-02
2025-02-04 13:00 | flat_start_nr | 144.93 | 4 | 506 | 2025-02
2025-02-04 14:00 | flat_start_nr | 149.2 | 6 | 526 | 2025-02
2025-02-04 15:00 | flat_start_nr | 137.92 | 4 | 536 | 2025-02
2025-02-04 16:00 | flat_start_nr | 147.9 | 4 | 520 | 2025-02
2025-02-04 17:00 | flat_start_nr | 151.3 | 5 | 536 | 2025-02
2025-02-04 18:00 | flat_start_nr | 127.78 | 2 | 550 | 2025-02
2025-02-04 19:00 | flat_start_nr | 136.81 | 3 | 551 | 2025-02
2025-02-04 20:00 | flat_start_nr | 153.55 | 5 | 527 | 2025-02
2025-02-04 21:00 | flat_start_nr | 155.82 | 5 | 552 | 2025-02
2025-02-04 22:00 | flat_start_nr | 153.62 | 6 | 547 | 2025-02
2025-02-04 23:00 | flat_start_nr | 153.61 | 6 | 543 | 2025-02
2025-02-05 | flat_start_nr | 137.27 | 4 | 527 | 2025-02
2025-02-05 01:00 | flat_start_nr | 135.15 | 4 | 525 | 2025-02
2025-02-05 02:00 | flat_start_nr | 134.49 | 4 | 525 | 2025-02
2025-02-05 03:00 | flat_start_nr | 136.75 | 3 | 525 | 2025-02
2025-02-05 04:00 | flat_start_nr | 136.85 | 3 | 526 | 2025-02
2025-02-05 05:00 | flat_start_nr | 137.31 | 3 | 527 | 2025-02
2025-02-05 06:00 | flat_start_nr | 135.92 | 3 | 528 | 2025-02
2025-02-05 07:00 | flat_start_nr | 130.99 | 3 | 532 | 2025-02
2025-02-05 08:00 | flat_start_nr | 141.47 | 3 | 534 | 2025-02
2025-02-05 09:00 | flat_start_nr | 148.86 | 5 | 513 | 2025-02
2025-02-05 10:00 | flat_start_nr | 145.29 | 3 | 512 | 2025-02
2025-02-05 11:00 | flat_start_nr | 148.18 | 5 | 509 | 2025-02
2025-02-05 12:00 | flat_start_nr | 146.31 | 5 | 508 | 2025-02
2025-02-05 13:00 | flat_start_nr | 150.36 | 6 | 524 | 2025-02
2025-02-05 16:00 | flat_start_nr | 140.27 | 5 | 531 | 2025-02
2025-02-05 17:00 | flat_start_nr | 133.25 | 5 | 530 | 2025-02
2025-02-05 18:00 | flat_start_nr | 135 | 5 | 531 | 2025-02
2025-02-05 19:00 | flat_start_nr | 139.42 | 5 | 540 | 2025-02
2025-02-05 20:00 | flat_start_nr | 141.88 | 5 | 540 | 2025-02
2025-02-05 21:00 | flat_start_nr | 143.93 | 5 | 535 | 2025-02
2025-02-05 22:00 | flat_start_nr | 143.74 | 5 | 539 | 2025-02
2025-02-05 23:00 | flat_start_nr | 140.91 | 5 | 543 | 2025-02
2025-02-06 | flat_start_nr | 138.36 | 5 | 535 | 2025-02
2025-02-06 01:00 | flat_start_nr | 140.49 | 4 | 538 | 2025-02
2025-02-06 02:00 | flat_start_nr | 140.2 | 5 | 541 | 2025-02
2025-02-06 03:00 | flat_start_nr | 140.08 | 4 | 537 | 2025-02
2025-02-06 04:00 | flat_start_nr | 139.5 | 5 | 545 | 2025-02
2025-02-06 05:00 | flat_start_nr | 137.27 | 5 | 542 | 2025-02
2025-02-06 06:00 | flat_start_nr | 127.75 | 4 | 540 | 2025-02
2025-02-06 07:00 | flat_start_nr | 116.6 | 4 | 535 | 2025-02
2025-02-06 08:00 | flat_start_nr | 130.17 | 6 | 539 | 2025-02
2025-02-06 09:00 | flat_start_nr | 138.48 | 6 | 535 | 2025-02
2025-02-06 10:00 | flat_start_nr | 150.48 | 7 | 520 | 2025-02
2025-02-06 11:00 | flat_start_nr | 146.28 | 6 | 509 | 2025-02
2025-02-06 17:00 | flat_start_nr | 141.35 | 5 | 536 | 2025-02
2025-02-06 18:00 | flat_start_nr | 122.45 | 4 | 532 | 2025-02
2025-02-06 19:00 | flat_start_nr | 121.82 | 4 | 536 | 2025-02
2025-02-06 20:00 | flat_start_nr | 118.57 | 4 | 531 | 2025-02
2025-02-06 21:00 | flat_start_nr | 123.16 | 4 | 529 | 2025-02
2025-02-06 22:00 | flat_start_nr | 133.94 | 5 | 523 | 2025-02
2025-02-06 23:00 | flat_start_nr | 147.55 | 6 | 517 | 2025-02
2025-02-07 | flat_start_nr | 140.71 | 5 | 526 | 2025-02
2025-02-07 01:00 | flat_start_nr | 124.09 | 4 | 528 | 2025-02
2025-02-07 02:00 | flat_start_nr | 125.59 | 4 | 526 | 2025-02
2025-02-07 03:00 | flat_start_nr | 126.26 | 4 | 526 | 2025-02
2025-02-07 04:00 | flat_start_nr | 130.21 | 5 | 522 | 2025-02
2025-02-07 05:00 | flat_start_nr | 126.33 | 4 | 526 | 2025-02
2025-02-07 06:00 | flat_start_nr | 134.25 | 3 | 530 | 2025-02
2025-02-07 07:00 | flat_start_nr | 136.51 | 3 | 536 | 2025-02
2025-02-07 08:00 | flat_start_nr | 151.87 | 5 | 542 | 2025-02
2025-02-07 09:00 | flat_start_nr | 138.43 | 4 | 538 | 2025-02
2025-02-07 10:00 | flat_start_nr | 141.2 | 5 | 514 | 2025-02
2025-02-07 11:00 | flat_start_nr | 150.01 | 7 | 525 | 2025-02
2025-02-07 16:00 | flat_start_nr | 151.21 | 7 | 523 | 2025-02
2025-02-07 17:00 | flat_start_nr | 148.07 | 6 | 510 | 2025-02
2025-02-07 18:00 | flat_start_nr | 148.31 | 6 | 519 | 2025-02
2025-02-07 19:00 | flat_start_nr | 148.19 | 6 | 522 | 2025-02
2025-02-07 20:00 | flat_start_nr | 146.54 | 6 | 519 | 2025-02
2025-02-07 21:00 | flat_start_nr | 143.33 | 5 | 526 | 2025-02
2025-02-07 22:00 | flat_start_nr | 139.34 | 5 | 528 | 2025-02
2025-02-07 23:00 | flat_start_nr | 137.82 | 6 | 526 | 2025-02
2025-02-08 | flat_start_nr | 145.03 | 6 | 524 | 2025-02
2025-02-08 01:00 | flat_start_nr | 134.69 | 6 | 528 | 2025-02
2025-02-08 02:00 | flat_start_nr | 132.53 | 6 | 527 | 2025-02
2025-02-08 03:00 | flat_start_nr | 130.89 | 6 | 528 | 2025-02
2025-02-08 04:00 | flat_start_nr | 132.16 | 6 | 527 | 2025-02
2025-02-08 05:00 | flat_start_nr | 132.58 | 6 | 529 | 2025-02
2025-02-08 06:00 | flat_start_nr | 134.78 | 6 | 533 | 2025-02
2025-02-08 07:00 | flat_start_nr | 135.9 | 6 | 536 | 2025-02
2025-02-08 08:00 | flat_start_nr | 136.14 | 5 | 526 | 2025-02
2025-02-08 09:00 | flat_start_nr | 127.96 | 4 | 529 | 2025-02
2025-02-08 10:00 | flat_start_nr | 127.13 | 4 | 534 | 2025-02
2025-02-08 11:00 | flat_start_nr | 134.35 | 5 | 524 | 2025-02
2025-02-08 12:00 | flat_start_nr | 148.93 | 5 | 514 | 2025-02
2025-02-08 15:00 | flat_start_nr | 152.61 | 6 | 524 | 2025-02
2025-02-08 16:00 | flat_start_nr | 150.22 | 6 | 532 | 2025-02
2025-02-08 17:00 | flat_start_nr | 143.56 | 4 | 512 | 2025-02
2025-02-08 18:00 | flat_start_nr | 133.48 | 4 | 528 | 2025-02
2025-02-08 19:00 | flat_start_nr | 135.6 | 4 | 530 | 2025-02
2025-02-08 20:00 | flat_start_nr | 141.61 | 4 | 540 | 2025-02
2025-02-08 21:00 | flat_start_nr | 141.1 | 5 | 543 | 2025-02
2025-02-08 22:00 | flat_start_nr | 130.89 | 5 | 530 | 2025-02
2025-02-08 23:00 | flat_start_nr | 128.56 | 4 | 530 | 2025-02
2025-02-09 | flat_start_nr | 137.96 | 4 | 533 | 2025-02
2025-02-09 01:00 | flat_start_nr | 142.75 | 4 | 540 | 2025-02
2025-02-09 02:00 | flat_start_nr | 137.97 | 4 | 537 | 2025-02
2025-02-09 03:00 | flat_start_nr | 136.69 | 4 | 531 | 2025-02
2025-02-09 04:00 | flat_start_nr | 134.61 | 4 | 529 | 2025-02
2025-02-09 05:00 | flat_start_nr | 132.88 | 4 | 530 | 2025-02
2025-02-09 06:00 | flat_start_nr | 133.96 | 4 | 536 | 2025-02
2025-02-09 07:00 | flat_start_nr | 133.47 | 4 | 529 | 2025-02
2025-02-09 08:00 | flat_start_nr | 146.14 | 6 | 520 | 2025-02
2025-02-09 09:00 | flat_start_nr | 147.65 | 5 | 513 | 2025-02
2025-02-09 10:00 | flat_start_nr | 148.56 | 5 | 514 | 2025-02
2025-02-09 11:00 | flat_start_nr | 138.69 | 4 | 530 | 2025-02
2025-02-09 12:00 | flat_start_nr | 131.36 | 5 | 523 | 2025-02
2025-02-09 13:00 | flat_start_nr | 127.41 | 4 | 522 | 2025-02
2025-02-09 14:00 | flat_start_nr | 138.2 | 5 | 522 | 2025-02
2025-02-09 15:00 | flat_start_nr | 140.79 | 4 | 526 | 2025-02
2025-02-09 16:00 | flat_start_nr | 138.75 | 4 | 523 | 2025-02
2025-02-09 17:00 | flat_start_nr | 134.57 | 4 | 517 | 2025-02
2025-02-09 18:00 | flat_start_nr | 127.54 | 3 | 526 | 2025-02
2025-02-09 19:00 | flat_start_nr | 137.19 | 4 | 530 | 2025-02
2025-02-09 20:00 | flat_start_nr | 140.39 | 4 | 529 | 2025-02
2025-02-09 21:00 | flat_start_nr | 135.66 | 4 | 526 | 2025-02
2025-02-09 22:00 | flat_start_nr | 138.14 | 4 | 529 | 2025-02
2025-02-09 23:00 | flat_start_nr | 142.13 | 4 | 526 | 2025-02
2025-02-10 | flat_start_nr | 137.88 | 5 | 522 | 2025-02
2025-02-10 01:00 | flat_start_nr | 132.6 | 5 | 524 | 2025-02
2025-02-10 02:00 | flat_start_nr | 134.42 | 5 | 525 | 2025-02
2025-02-10 03:00 | flat_start_nr | 133.24 | 5 | 525 | 2025-02
2025-02-10 04:00 | flat_start_nr | 123.16 | 3 | 520 | 2025-02
2025-02-10 05:00 | flat_start_nr | 121.76 | 3 | 524 | 2025-02
2025-02-10 06:00 | flat_start_nr | 124.51 | 4 | 526 | 2025-02
2025-02-10 07:00 | flat_start_nr | 120.36 | 4 | 523 | 2025-02
2025-02-10 08:00 | flat_start_nr | 136.16 | 5 | 519 | 2025-02
2025-02-10 09:00 | flat_start_nr | 139.65 | 5 | 526 | 2025-02
2025-02-10 17:00 | flat_start_nr | 138.88 | 5 | 535 | 2025-02
2025-02-10 18:00 | flat_start_nr | 122.42 | 4 | 530 | 2025-02
2025-02-10 19:00 | flat_start_nr | 128.24 | 4 | 530 | 2025-02
2025-02-10 20:00 | flat_start_nr | 126.89 | 4 | 530 | 2025-02
2025-02-10 21:00 | flat_start_nr | 122.81 | 4 | 531 | 2025-02
2025-02-10 22:00 | flat_start_nr | 126.66 | 4 | 530 | 2025-02
2025-02-10 23:00 | flat_start_nr | 131.31 | 5 | 531 | 2025-02
2025-02-11 | flat_start_nr | 133.1 | 5 | 529 | 2025-02
2025-02-11 01:00 | flat_start_nr | 137.47 | 5 | 530 | 2025-02
2025-02-11 02:00 | flat_start_nr | 140.22 | 4 | 532 | 2025-02
2025-02-11 03:00 | flat_start_nr | 140.58 | 4 | 532 | 2025-02
2025-02-11 04:00 | flat_start_nr | 137.83 | 5 | 534 | 2025-02
2025-02-11 05:00 | flat_start_nr | 129.59 | 4 | 530 | 2025-02
2025-02-11 06:00 | flat_start_nr | 122.04 | 3 | 526 | 2025-02
2025-02-11 07:00 | flat_start_nr | 120.48 | 3 | 530 | 2025-02
2025-02-11 08:00 | flat_start_nr | 130.79 | 5 | 522 | 2025-02
2025-02-11 09:00 | flat_start_nr | 135.94 | 5 | 524 | 2025-02
2025-02-11 10:00 | flat_start_nr | 138.29 | 5 | 530 | 2025-02
2025-02-11 11:00 | flat_start_nr | 134.09 | 5 | 526 | 2025-02
2025-02-11 12:00 | flat_start_nr | 129.43 | 5 | 525 | 2025-02
2025-02-11 13:00 | flat_start_nr | 141.24 | 4 | 532 | 2025-02
2025-02-11 16:00 | flat_start_nr | 151.04 | 6 | 513 | 2025-02
2025-02-11 17:00 | flat_start_nr | 133.46 | 5 | 524 | 2025-02
2025-02-11 18:00 | flat_start_nr | 123.6 | 3 | 529 | 2025-02
2025-02-11 19:00 | flat_start_nr | 129.93 | 4 | 535 | 2025-02
2025-02-11 20:00 | flat_start_nr | 138.53 | 3 | 535 | 2025-02
2025-02-11 21:00 | flat_start_nr | 137.34 | 3 | 530 | 2025-02
2025-02-11 22:00 | flat_start_nr | 137.86 | 4 | 529 | 2025-02
2025-02-11 23:00 | flat_start_nr | 146.34 | 4 | 520 | 2025-02
2025-02-12 | flat_start_nr | 144.08 | 4 | 526 | 2025-02
2025-02-12 01:00 | flat_start_nr | 145.79 | 5 | 526 | 2025-02
2025-02-12 02:00 | flat_start_nr | 145.66 | 5 | 525 | 2025-02
2025-02-12 03:00 | flat_start_nr | 145.59 | 5 | 525 | 2025-02
2025-02-12 04:00 | flat_start_nr | 150.77 | 5 | 508 | 2025-02
2025-02-12 05:00 | flat_start_nr | 149.89 | 5 | 509 | 2025-02
2025-02-12 06:00 | flat_start_nr | 146.08 | 5 | 519 | 2025-02
2025-02-12 07:00 | flat_start_nr | 131.35 | 5 | 527 | 2025-02
2025-02-12 08:00 | flat_start_nr | 138.85 | 5 | 531 | 2025-02
2025-02-12 10:00 | flat_start_nr | 149.57 | 6 | 513 | 2025-02
2025-02-12 11:00 | flat_start_nr | 141.35 | 4 | 533 | 2025-02
2025-02-12 12:00 | flat_start_nr | 149.29 | 5 | 512 | 2025-02
2025-02-12 13:00 | flat_start_nr | 148.89 | 5 | 509 | 2025-02
2025-02-12 14:00 | flat_start_nr | 150 | 5 | 510 | 2025-02
2025-02-12 15:00 | flat_start_nr | 150.61 | 6 | 506 | 2025-02
2025-02-12 16:00 | flat_start_nr | 146.57 | 6 | 505 | 2025-02
2025-02-12 17:00 | flat_start_nr | 150.73 | 7 | 504 | 2025-02
2025-02-12 18:00 | flat_start_nr | 133.95 | 5 | 529 | 2025-02
2025-02-12 19:00 | flat_start_nr | 132.17 | 5 | 528 | 2025-02
2025-02-12 20:00 | flat_start_nr | 133.46 | 5 | 529 | 2025-02
2025-02-12 21:00 | flat_start_nr | 128.74 | 4 | 519 | 2025-02
2025-02-12 22:00 | flat_start_nr | 134.6 | 5 | 520 | 2025-02
2025-02-12 23:00 | flat_start_nr | 140.76 | 5 | 522 | 2025-02
2025-02-13 | flat_start_nr | 141.4 | 4 | 527 | 2025-02
2025-02-13 01:00 | flat_start_nr | 144.33 | 4 | 523 | 2025-02
2025-02-13 02:00 | flat_start_nr | 145.73 | 5 | 517 | 2025-02
2025-02-13 03:00 | flat_start_nr | 148.17 | 5 | 511 | 2025-02
2025-02-13 04:00 | flat_start_nr | 146.36 | 5 | 512 | 2025-02
2025-02-13 05:00 | flat_start_nr | 152.58 | 6 | 526 | 2025-02
2025-02-13 06:00 | flat_start_nr | 150.7 | 6 | 503 | 2025-02
2025-02-13 07:00 | flat_start_nr | 145.18 | 5 | 519 | 2025-02
2025-02-13 08:00 | flat_start_nr | 141.75 | 5 | 506 | 2025-02
2025-02-13 09:00 | flat_start_nr | 139.37 | 5 | 527 | 2025-02
2025-02-13 10:00 | flat_start_nr | 134.79 | 5 | 528 | 2025-02
2025-02-13 11:00 | flat_start_nr | 136.2 | 5 | 527 | 2025-02
2025-02-13 12:00 | flat_start_nr | 141.44 | 5 | 519 | 2025-02
2025-02-13 13:00 | flat_start_nr | 145.2 | 4 | 510 | 2025-02
2025-02-13 14:00 | flat_start_nr | 146.28 | 6 | 500 | 2025-02
2025-02-13 15:00 | gauss | 153.49 | 7 | 532 | 2025-02
2025-02-13 16:00 | flat_start_nr | 144.48 | 4 | 511 | 2025-02
2025-02-13 17:00 | flat_start_nr | 138.2 | 5 | 516 | 2025-02
2025-02-13 18:00 | flat_start_nr | 126.69 | 4 | 518 | 2025-02
2025-02-13 19:00 | flat_start_nr | 125.81 | 4 | 519 | 2025-02
2025-02-13 20:00 | flat_start_nr | 120.43 | 4 | 526 | 2025-02
2025-02-13 21:00 | flat_start_nr | 122.26 | 4 | 525 | 2025-02
2025-02-13 22:00 | flat_start_nr | 120.31 | 4 | 527 | 2025-02
2025-02-13 23:00 | flat_start_nr | 127.54 | 4 | 521 | 2025-02
2025-02-14 | flat_start_nr | 130.05 | 4 | 519 | 2025-02
2025-02-14 01:00 | flat_start_nr | 138.74 | 5 | 521 | 2025-02
2025-02-14 02:00 | flat_start_nr | 138.36 | 5 | 522 | 2025-02
2025-02-14 03:00 | flat_start_nr | 130.14 | 4 | 520 | 2025-02
2025-02-14 04:00 | flat_start_nr | 130.69 | 4 | 520 | 2025-02
2025-02-14 05:00 | flat_start_nr | 138.92 | 4 | 524 | 2025-02
2025-02-14 06:00 | flat_start_nr | 127.24 | 3 | 522 | 2025-02
2025-02-14 07:00 | flat_start_nr | 124.5 | 4 | 521 | 2025-02
2025-02-14 08:00 | flat_start_nr | 144.29 | 4 | 511 | 2025-02
2025-02-14 09:00 | flat_start_nr | 142.44 | 5 | 509 | 2025-02
2025-02-14 10:00 | flat_start_nr | 145.95 | 5 | 508 | 2025-02
2025-02-14 11:00 | flat_start_nr | 145.41 | 4 | 507 | 2025-02
2025-02-14 14:00 | flat_start_nr | 149.84 | 6 | 523 | 2025-02
2025-02-14 18:00 | flat_start_nr | 127.04 | 4 | 524 | 2025-02
2025-02-14 19:00 | flat_start_nr | 125.62 | 4 | 522 | 2025-02
2025-02-14 20:00 | flat_start_nr | 122.99 | 4 | 527 | 2025-02
2025-02-14 21:00 | flat_start_nr | 122.8 | 4 | 528 | 2025-02
2025-02-14 22:00 | flat_start_nr | 125.02 | 4 | 522 | 2025-02
2025-02-14 23:00 | flat_start_nr | 131.63 | 5 | 520 | 2025-02
2025-02-15 | flat_start_nr | 129.64 | 5 | 522 | 2025-02
2025-02-15 01:00 | flat_start_nr | 126.3 | 3 | 526 | 2025-02
2025-02-15 02:00 | flat_start_nr | 121.66 | 3 | 522 | 2025-02
2025-02-15 03:00 | flat_start_nr | 122.67 | 3 | 526 | 2025-02
2025-02-15 04:00 | flat_start_nr | 121.63 | 3 | 526 | 2025-02
2025-02-15 05:00 | flat_start_nr | 122.51 | 3 | 526 | 2025-02
2025-02-15 06:00 | flat_start_nr | 117.91 | 3 | 526 | 2025-02
2025-02-15 07:00 | flat_start_nr | 121.96 | 3 | 524 | 2025-02
2025-02-15 08:00 | flat_start_nr | 135.12 | 4 | 520 | 2025-02
2025-02-15 09:00 | flat_start_nr | 133.1 | 5 | 523 | 2025-02
2025-02-15 10:00 | flat_start_nr | 132.69 | 5 | 523 | 2025-02
2025-02-15 11:00 | flat_start_nr | 132.14 | 5 | 520 | 2025-02
2025-02-15 12:00 | flat_start_nr | 130.82 | 5 | 521 | 2025-02
2025-02-15 13:00 | flat_start_nr | 136.17 | 4 | 521 | 2025-02
2025-02-15 14:00 | flat_start_nr | 137.61 | 4 | 522 | 2025-02
2025-02-15 15:00 | flat_start_nr | 152.67 | 6 | 522 | 2025-02
2025-02-15 18:00 | flat_start_nr | 143.49 | 3 | 541 | 2025-02
2025-02-15 19:00 | flat_start_nr | 134.98 | 4 | 540 | 2025-02
2025-02-15 20:00 | flat_start_nr | 130.49 | 4 | 539 | 2025-02
2025-02-15 21:00 | flat_start_nr | 131.93 | 4 | 540 | 2025-02
2025-02-15 22:00 | flat_start_nr | 129.31 | 4 | 538 | 2025-02
2025-02-15 23:00 | flat_start_nr | 133.1 | 4 | 536 | 2025-02
2025-02-16 | flat_start_nr | 133.91 | 4 | 533 | 2025-02
2025-02-16 01:00 | flat_start_nr | 129.17 | 3 | 531 | 2025-02
2025-02-16 02:00 | flat_start_nr | 126.83 | 3 | 526 | 2025-02
2025-02-16 03:00 | flat_start_nr | 126.97 | 3 | 525 | 2025-02
2025-02-16 04:00 | flat_start_nr | 127.11 | 3 | 526 | 2025-02
2025-02-16 05:00 | flat_start_nr | 125.97 | 3 | 525 | 2025-02
2025-02-16 06:00 | flat_start_nr | 119.6 | 3 | 527 | 2025-02
2025-02-16 07:00 | flat_start_nr | 118.77 | 3 | 526 | 2025-02
2025-02-16 08:00 | flat_start_nr | 133.33 | 4 | 524 | 2025-02
2025-02-16 09:00 | flat_start_nr | 138.63 | 4 | 521 | 2025-02
2025-02-16 10:00 | flat_start_nr | 136.94 | 4 | 519 | 2025-02
2025-02-16 11:00 | flat_start_nr | 138.15 | 4 | 522 | 2025-02
2025-02-16 12:00 | flat_start_nr | 137.97 | 4 | 528 | 2025-02
2025-02-16 13:00 | flat_start_nr | 145.39 | 4 | 509 | 2025-02
2025-02-16 14:00 | flat_start_nr | 149.89 | 6 | 516 | 2025-02
2025-02-16 15:00 | flat_start_nr | 149.66 | 6 | 534 | 2025-02
2025-02-16 17:00 | flat_start_nr | 150.6 | 6 | 531 | 2025-02
2025-02-16 18:00 | flat_start_nr | 133.95 | 4 | 539 | 2025-02
2025-02-16 19:00 | flat_start_nr | 134.61 | 4 | 535 | 2025-02
2025-02-16 20:00 | flat_start_nr | 132.29 | 4 | 537 | 2025-02
2025-02-16 21:00 | flat_start_nr | 131.83 | 4 | 537 | 2025-02
2025-02-16 22:00 | flat_start_nr | 127.71 | 3 | 534 | 2025-02
2025-02-16 23:00 | flat_start_nr | 130.32 | 4 | 536 | 2025-02
2025-02-17 | flat_start_nr | 130.6 | 4 | 535 | 2025-02
2025-02-17 01:00 | flat_start_nr | 129 | 4 | 537 | 2025-02
2025-02-17 02:00 | flat_start_nr | 128.47 | 4 | 540 | 2025-02
2025-02-17 03:00 | flat_start_nr | 128.01 | 3 | 539 | 2025-02
2025-02-17 04:00 | flat_start_nr | 129.29 | 4 | 537 | 2025-02
2025-02-17 05:00 | flat_start_nr | 127.31 | 3 | 538 | 2025-02
2025-02-17 06:00 | flat_start_nr | 130.44 | 4 | 536 | 2025-02
2025-02-17 07:00 | flat_start_nr | 131.16 | 4 | 536 | 2025-02
2025-02-17 08:00 | flat_start_nr | 142.46 | 4 | 540 | 2025-02
2025-02-17 09:00 | flat_start_nr | 143.79 | 4 | 534 | 2025-02
2025-02-17 10:00 | flat_start_nr | 140.13 | 4 | 533 | 2025-02
2025-02-17 11:00 | flat_start_nr | 141.12 | 4 | 538 | 2025-02
2025-02-17 12:00 | flat_start_nr | 140.48 | 4 | 535 | 2025-02
2025-02-17 13:00 | flat_start_nr | 141.49 | 4 | 541 | 2025-02
2025-02-17 14:00 | flat_start_nr | 143.54 | 4 | 538 | 2025-02
2025-02-17 15:00 | flat_start_nr | 146.32 | 5 | 522 | 2025-02
2025-02-17 16:00 | flat_start_nr | 143.6 | 4 | 541 | 2025-02
2025-02-17 17:00 | flat_start_nr | 141.84 | 4 | 545 | 2025-02
2025-02-17 18:00 | flat_start_nr | 125.45 | 3 | 538 | 2025-02
2025-02-17 19:00 | flat_start_nr | 127.64 | 3 | 540 | 2025-02
2025-02-17 20:00 | flat_start_nr | 125.27 | 3 | 541 | 2025-02
2025-02-17 21:00 | flat_start_nr | 123.05 | 4 | 544 | 2025-02
2025-02-17 22:00 | flat_start_nr | 126.03 | 3 | 546 | 2025-02
2025-02-17 23:00 | flat_start_nr | 130.24 | 4 | 543 | 2025-02
2025-02-18 | flat_start_nr | 131.73 | 4 | 543 | 2025-02
2025-02-18 01:00 | flat_start_nr | 130.03 | 5 | 540 | 2025-02
2025-02-18 02:00 | flat_start_nr | 132.73 | 4 | 540 | 2025-02
2025-02-18 03:00 | flat_start_nr | 132.58 | 5 | 540 | 2025-02
2025-02-18 04:00 | flat_start_nr | 135.68 | 4 | 541 | 2025-02
2025-02-18 05:00 | flat_start_nr | 135.48 | 4 | 540 | 2025-02
2025-02-18 06:00 | flat_start_nr | 121.51 | 5 | 538 | 2025-02
2025-02-18 07:00 | flat_start_nr | 116.79 | 3 | 540 | 2025-02
2025-02-18 08:00 | flat_start_nr | 133.08 | 5 | 525 | 2025-02
2025-02-18 09:00 | flat_start_nr | 142.38 | 4 | 541 | 2025-02
2025-02-18 10:00 | flat_start_nr | 145.84 | 5 | 521 | 2025-02
2025-02-18 11:00 | flat_start_nr | 126.7 | 4 | 526 | 2025-02
2025-02-18 12:00 | flat_start_nr | 124.55 | 4 | 533 | 2025-02
2025-02-18 13:00 | flat_start_nr | 129.37 | 5 | 532 | 2025-02
2025-02-18 14:00 | flat_start_nr | 132.71 | 5 | 533 | 2025-02
2025-02-18 15:00 | flat_start_nr | 128.83 | 4 | 532 | 2025-02
2025-02-18 16:00 | flat_start_nr | 128.85 | 4 | 531 | 2025-02
2025-02-18 17:00 | flat_start_nr | 126.62 | 5 | 534 | 2025-02
2025-02-18 18:00 | flat_start_nr | 119.79 | 4 | 545 | 2025-02
2025-02-18 19:00 | flat_start_nr | 119.1 | 3 | 542 | 2025-02
2025-02-18 20:00 | flat_start_nr | 124.04 | 4 | 542 | 2025-02
2025-02-18 21:00 | flat_start_nr | 122.47 | 4 | 541 | 2025-02
2025-02-18 22:00 | flat_start_nr | 128.36 | 4 | 542 | 2025-02
2025-02-18 23:00 | flat_start_nr | 127.41 | 4 | 541 | 2025-02
2025-02-19 | flat_start_nr | 132.77 | 6 | 546 | 2025-02
2025-02-19 01:00 | flat_start_nr | 130.9 | 4 | 553 | 2025-02
2025-02-19 02:00 | flat_start_nr | 130.63 | 4 | 555 | 2025-02
2025-02-19 03:00 | flat_start_nr | 129.43 | 4 | 547 | 2025-02
2025-02-19 04:00 | flat_start_nr | 128.81 | 4 | 545 | 2025-02
2025-02-19 05:00 | flat_start_nr | 127.5 | 4 | 551 | 2025-02
2025-02-19 06:00 | flat_start_nr | 130.98 | 4 | 551 | 2025-02
2025-02-19 07:00 | flat_start_nr | 137.78 | 4 | 542 | 2025-02
2025-02-19 08:00 | flat_start_nr | 135.24 | 5 | 543 | 2025-02
2025-02-19 10:00 | flat_start_nr | 152.85 | 6 | 541 | 2025-02
2025-02-19 11:00 | flat_start_nr | 142.52 | 4 | 551 | 2025-02
2025-02-19 12:00 | flat_start_nr | 136.78 | 4 | 541 | 2025-02
2025-02-19 13:00 | flat_start_nr | 134.47 | 4 | 544 | 2025-02
2025-02-19 14:00 | flat_start_nr | 138.05 | 4 | 541 | 2025-02
2025-02-19 15:00 | flat_start_nr | 134.92 | 4 | 540 | 2025-02
2025-02-19 16:00 | flat_start_nr | 133.71 | 4 | 541 | 2025-02
2025-02-19 17:00 | flat_start_nr | 126.52 | 4 | 533 | 2025-02
2025-02-19 18:00 | flat_start_nr | 119.99 | 4 | 541 | 2025-02
2025-02-19 19:00 | flat_start_nr | 120.14 | 4 | 543 | 2025-02
2025-02-19 20:00 | flat_start_nr | 116.35 | 4 | 542 | 2025-02
2025-02-19 21:00 | flat_start_nr | 119.35 | 3 | 542 | 2025-02
2025-02-19 22:00 | flat_start_nr | 119.98 | 4 | 543 | 2025-02
2025-02-19 23:00 | flat_start_nr | 127.99 | 4 | 539 | 2025-02
2025-02-20 | flat_start_nr | 131.57 | 5 | 541 | 2025-02
2025-02-20 01:00 | flat_start_nr | 131.73 | 5 | 541 | 2025-02
2025-02-20 02:00 | flat_start_nr | 129 | 4 | 541 | 2025-02
2025-02-20 03:00 | flat_start_nr | 128.07 | 4 | 544 | 2025-02
2025-02-20 04:00 | flat_start_nr | 127.45 | 4 | 541 | 2025-02
2025-02-20 05:00 | flat_start_nr | 127.41 | 4 | 536 | 2025-02
2025-02-20 06:00 | flat_start_nr | 129.4 | 4 | 538 | 2025-02
2025-02-20 07:00 | flat_start_nr | 133.58 | 4 | 531 | 2025-02
2025-02-20 08:00 | flat_start_nr | 133.63 | 5 | 527 | 2025-02
2025-02-20 09:00 | flat_start_nr | 130.75 | 4 | 526 | 2025-02
2025-02-20 10:00 | flat_start_nr | 134.37 | 4 | 533 | 2025-02
2025-02-20 11:00 | flat_start_nr | 146.85 | 5 | 524 | 2025-02
2025-02-20 14:00 | flat_start_nr | 155.74 | 6 | 534 | 2025-02
2025-02-20 15:00 | flat_start_nr | 149.37 | 5 | 531 | 2025-02
2025-02-20 16:00 | flat_start_nr | 148.07 | 5 | 523 | 2025-02
2025-02-20 17:00 | flat_start_nr | 135.65 | 5 | 527 | 2025-02
2025-02-20 18:00 | flat_start_nr | 126 | 4 | 541 | 2025-02
2025-02-20 19:00 | flat_start_nr | 119.59 | 4 | 538 | 2025-02
2025-02-20 20:00 | flat_start_nr | 120.18 | 4 | 538 | 2025-02
2025-02-20 21:00 | flat_start_nr | 130.34 | 5 | 538 | 2025-02
2025-02-20 22:00 | flat_start_nr | 138.64 | 5 | 544 | 2025-02
2025-02-20 23:00 | flat_start_nr | 146.54 | 6 | 539 | 2025-02
2025-02-21 | flat_start_nr | 146.64 | 6 | 539 | 2025-02
2025-02-21 01:00 | flat_start_nr | 148.63 | 6 | 530 | 2025-02
2025-02-21 02:00 | flat_start_nr | 152.69 | 7 | 529 | 2025-02
2025-02-21 03:00 | flat_start_nr | 151.85 | 6 | 528 | 2025-02
2025-02-21 04:00 | flat_start_nr | 151.44 | 6 | 530 | 2025-02
2025-02-21 05:00 | flat_start_nr | 149.02 | 6 | 530 | 2025-02
2025-02-21 06:00 | flat_start_nr | 144.85 | 5 | 545 | 2025-02
2025-02-21 07:00 | flat_start_nr | 146.06 | 6 | 540 | 2025-02
2025-02-21 08:00 | flat_start_nr | 146.12 | 5 | 527 | 2025-02
2025-02-21 09:00 | flat_start_nr | 150.95 | 6 | 525 | 2025-02
2025-02-21 10:00 | flat_start_nr | 150.41 | 5 | 527 | 2025-02
2025-02-21 11:00 | flat_start_nr | 151.29 | 6 | 526 | 2025-02
2025-02-21 12:00 | flat_start_nr | 155.9 | 6 | 534 | 2025-02
2025-02-21 17:00 | flat_start_nr | 145.82 | 5 | 521 | 2025-02
2025-02-21 18:00 | flat_start_nr | 128.65 | 3 | 534 | 2025-02
2025-02-21 19:00 | flat_start_nr | 128.69 | 4 | 532 | 2025-02
2025-02-21 20:00 | flat_start_nr | 130.97 | 4 | 531 | 2025-02
2025-02-21 21:00 | flat_start_nr | 130.6 | 4 | 536 | 2025-02
2025-02-21 22:00 | flat_start_nr | 133.42 | 6 | 536 | 2025-02
2025-02-21 23:00 | flat_start_nr | 136.35 | 6 | 536 | 2025-02
2025-02-22 | flat_start_nr | 147.74 | 7 | 529 | 2025-02
2025-02-22 01:00 | flat_start_nr | 152.55 | 8 | 518 | 2025-02
2025-02-22 02:00 | flat_start_nr | 154.6 | 8 | 523 | 2025-02
2025-02-22 03:00 | flat_start_nr | 152.21 | 6 | 520 | 2025-02
2025-02-22 04:00 | flat_start_nr | 145.5 | 6 | 530 | 2025-02
2025-02-22 05:00 | flat_start_nr | 148.68 | 6 | 523 | 2025-02
2025-02-22 06:00 | flat_start_nr | 148.9 | 6 | 527 | 2025-02
2025-02-22 18:00 | flat_start_nr | 139.9 | 5 | 528 | 2025-02
2025-02-22 19:00 | flat_start_nr | 144.2 | 5 | 529 | 2025-02
2025-02-22 20:00 | flat_start_nr | 139.58 | 5 | 530 | 2025-02
2025-02-22 21:00 | flat_start_nr | 153.66 | 7 | 520 | 2025-02
2025-02-23 | flat_start_nr | 156.94 | 7 | 542 | 2025-02
2025-02-23 19:00 | flat_start_nr | 151.53 | 6 | 535 | 2025-02
2025-02-23 20:00 | flat_start_nr | 155.56 | 7 | 527 | 2025-02
2025-02-23 21:00 | flat_start_nr | 140.87 | 5 | 543 | 2025-02
2025-02-23 22:00 | flat_start_nr | 147.42 | 6 | 536 | 2025-02
2025-02-24 | flat_start_nr | 151.76 | 6 | 530 | 2025-02
2025-02-24 01:00 | flat_start_nr | 137.58 | 5 | 547 | 2025-02
2025-02-24 02:00 | flat_start_nr | 134.88 | 5 | 537 | 2025-02
2025-02-24 03:00 | flat_start_nr | 146.6 | 5 | 538 | 2025-02
2025-02-24 04:00 | flat_start_nr | 153.16 | 6 | 526 | 2025-02
2025-02-24 05:00 | flat_start_nr | 153.13 | 6 | 530 | 2025-02
2025-02-24 06:00 | flat_start_nr | 152.76 | 6 | 535 | 2025-02
2025-02-24 11:00 | flat_start_nr | 156.96 | 6 | 549 | 2025-02
2025-02-24 17:00 | flat_start_nr | 152.24 | 6 | 523 | 2025-02
2025-02-24 18:00 | flat_start_nr | 130.45 | 4 | 538 | 2025-02
2025-02-24 19:00 | flat_start_nr | 122.5 | 3 | 534 | 2025-02
2025-02-24 20:00 | flat_start_nr | 117.87 | 3 | 540 | 2025-02
2025-02-24 21:00 | flat_start_nr | 117.65 | 3 | 542 | 2025-02
2025-02-24 22:00 | flat_start_nr | 118.06 | 4 | 534 | 2025-02
2025-02-24 23:00 | flat_start_nr | 129.15 | 3 | 538 | 2025-02
2025-02-25 | flat_start_nr | 131.18 | 6 | 534 | 2025-02
2025-02-25 01:00 | flat_start_nr | 130.45 | 5 | 536 | 2025-02
2025-02-25 02:00 | flat_start_nr | 141.11 | 4 | 537 | 2025-02
2025-02-25 03:00 | flat_start_nr | 138.47 | 5 | 537 | 2025-02
2025-02-25 04:00 | flat_start_nr | 139.17 | 4 | 539 | 2025-02
2025-02-25 05:00 | flat_start_nr | 139.32 | 5 | 533 | 2025-02
2025-02-25 06:00 | flat_start_nr | 132.64 | 5 | 539 | 2025-02
2025-02-25 07:00 | flat_start_nr | 131.73 | 6 | 532 | 2025-02
2025-02-25 08:00 | flat_start_nr | 144.09 | 4 | 527 | 2025-02
2025-02-25 18:00 | flat_start_nr | 137.94 | 5 | 526 | 2025-02
2025-02-25 19:00 | flat_start_nr | 134.8 | 5 | 522 | 2025-02
2025-02-25 20:00 | flat_start_nr | 139.24 | 6 | 524 | 2025-02
2025-02-25 21:00 | flat_start_nr | 144.41 | 6 | 522 | 2025-02
2025-02-25 22:00 | flat_start_nr | 151.28 | 7 | 515 | 2025-02
2025-02-25 23:00 | flat_start_nr | 148.49 | 7 | 519 | 2025-02
2025-02-26 06:00 | flat_start_nr | 146.58 | 6 | 525 | 2025-02
2025-02-26 07:00 | flat_start_nr | 151.91 | 6 | 510 | 2025-02
2025-02-26 08:00 | flat_start_nr | 153.78 | 6 | 516 | 2025-02
2025-02-26 09:00 | flat_start_nr | 153.29 | 6 | 518 | 2025-02
2025-02-26 10:00 | flat_start_nr | 154.98 | 6 | 544 | 2025-02
2025-02-26 11:00 | flat_start_nr | 153.19 | 6 | 524 | 2025-02
2025-02-26 12:00 | flat_start_nr | 150.97 | 6 | 518 | 2025-02
2025-02-26 13:00 | flat_start_nr | 150.01 | 5 | 527 | 2025-02
2025-02-26 14:00 | flat_start_nr | 153.79 | 6 | 528 | 2025-02
2025-02-26 16:00 | flat_start_nr | 152.8 | 6 | 516 | 2025-02
2025-02-26 17:00 | flat_start_nr | 154.18 | 6 | 530 | 2025-02
2025-02-26 18:00 | flat_start_nr | 139.95 | 5 | 534 | 2025-02
2025-02-26 19:00 | flat_start_nr | 135.31 | 5 | 537 | 2025-02
2025-02-26 20:00 | flat_start_nr | 132.28 | 5 | 539 | 2025-02
2025-02-26 21:00 | flat_start_nr | 135.02 | 5 | 539 | 2025-02
2025-02-26 22:00 | flat_start_nr | 139.93 | 5 | 538 | 2025-02
2025-02-26 23:00 | flat_start_nr | 158.42 | 7 | 537 | 2025-02
2025-02-27 06:00 | flat_start_nr | 158.47 | 7 | 533 | 2025-02
2025-02-27 18:00 | flat_start_nr | 133.91 | 4 | 541 | 2025-02
2025-02-27 19:00 | flat_start_nr | 126.47 | 3 | 532 | 2025-02
2025-02-27 20:00 | flat_start_nr | 124.87 | 3 | 542 | 2025-02
2025-02-27 21:00 | flat_start_nr | 127.69 | 3 | 543 | 2025-02
2025-02-27 22:00 | flat_start_nr | 135.23 | 4 | 551 | 2025-02
2025-02-27 23:00 | flat_start_nr | 138.8 | 4 | 549 | 2025-02
2025-02-28 | flat_start_nr | 151.02 | 5 | 534 | 2025-02
2025-02-28 01:00 | flat_start_nr | 155.88 | 6 | 561 | 2025-02
2025-02-28 02:00 | flat_start_nr | 151.86 | 6 | 538 | 2025-02
2025-02-28 03:00 | flat_start_nr | 143.67 | 4 | 548 | 2025-02
2025-02-28 04:00 | flat_start_nr | 138.09 | 4 | 551 | 2025-02
2025-02-28 05:00 | flat_start_nr | 138.56 | 4 | 555 | 2025-02
2025-02-28 06:00 | flat_start_nr | 121.62 | 4 | 550 | 2025-02
2025-02-28 07:00 | flat_start_nr | 123.63 | 4 | 536 | 2025-02
2025-02-28 08:00 | flat_start_nr | 136.25 | 4 | 536 | 2025-02
2025-02-28 09:00 | flat_start_nr | 153.4 | 6 | 559 | 2025-02
2025-02-28 18:00 | flat_start_nr | 143.55 | 4 | 543 | 2025-02
2025-02-28 19:00 | flat_start_nr | 143.19 | 4 | 540 | 2025-02
2025-02-28 20:00 | flat_start_nr | 129.11 | 3 | 536 | 2025-02
2025-02-28 21:00 | flat_start_nr | 120.43 | 3 | 532 | 2025-02
2025-02-28 22:00 | flat_start_nr | 120.27 | 3 | 531 | 2025-02
2025-02-28 23:00 | flat_start_nr | 123.21 | 3 | 527 | 2025-02
2025-03-01 | flat_start_nr | 125.27 | 3 | 525 | 2025-03
2025-03-01 01:00 | flat_start_nr | 132.01 | 4 | 533 | 2025-03
2025-03-01 02:00 | flat_start_nr | 134.11 | 4 | 540 | 2025-03
2025-03-01 03:00 | flat_start_nr | 139.28 | 5 | 542 | 2025-03
2025-03-01 04:00 | flat_start_nr | 136.95 | 5 | 542 | 2025-03
2025-03-01 05:00 | flat_start_nr | 134.08 | 6 | 540 | 2025-03
2025-03-01 06:00 | flat_start_nr | 133.03 | 4 | 538 | 2025-03
2025-03-01 07:00 | flat_start_nr | 143.88 | 4 | 541 | 2025-03
2025-03-01 08:00 | flat_start_nr | 146.35 | 5 | 526 | 2025-03
2025-03-01 12:00 | flat_start_nr | 151.04 | 6 | 520 | 2025-03
2025-03-01 13:00 | flat_start_nr | 152.55 | 6 | 525 | 2025-03
2025-03-01 17:00 | flat_start_nr | 151.89 | 6 | 541 | 2025-03
2025-03-01 18:00 | flat_start_nr | 129.99 | 5 | 539 | 2025-03
2025-03-01 19:00 | flat_start_nr | 123.1 | 4 | 535 | 2025-03
2025-03-01 20:00 | flat_start_nr | 131.89 | 5 | 536 | 2025-03
2025-03-01 21:00 | flat_start_nr | 133.2 | 5 | 536 | 2025-03
2025-03-01 22:00 | flat_start_nr | 130.16 | 5 | 537 | 2025-03
2025-03-01 23:00 | flat_start_nr | 131.32 | 5 | 539 | 2025-03
2025-03-02 | flat_start_nr | 128.84 | 3 | 536 | 2025-03
2025-03-02 01:00 | flat_start_nr | 126.74 | 3 | 534 | 2025-03
2025-03-02 02:00 | flat_start_nr | 122.77 | 3 | 531 | 2025-03
2025-03-02 03:00 | flat_start_nr | 117.71 | 3 | 539 | 2025-03
2025-03-02 04:00 | flat_start_nr | 120.43 | 3 | 534 | 2025-03
2025-03-02 05:00 | flat_start_nr | 127.25 | 3 | 532 | 2025-03
2025-03-02 06:00 | flat_start_nr | 121.38 | 3 | 533 | 2025-03
2025-03-02 07:00 | flat_start_nr | 134.62 | 4 | 529 | 2025-03
2025-03-02 08:00 | flat_start_nr | 138.95 | 4 | 537 | 2025-03
2025-03-02 09:00 | flat_start_nr | 150.72 | 6 | 522 | 2025-03
2025-03-02 10:00 | flat_start_nr | 141.62 | 4 | 545 | 2025-03
2025-03-02 11:00 | flat_start_nr | 131.44 | 4 | 535 | 2025-03
2025-03-02 12:00 | flat_start_nr | 119.87 | 3 | 531 | 2025-03
2025-03-02 13:00 | flat_start_nr | 119.25 | 3 | 532 | 2025-03
2025-03-02 14:00 | flat_start_nr | 131.31 | 4 | 532 | 2025-03
2025-03-02 15:00 | flat_start_nr | 141.39 | 4 | 534 | 2025-03
2025-03-02 16:00 | flat_start_nr | 153.76 | 6 | 540 | 2025-03
2025-03-02 17:00 | flat_start_nr | 142.99 | 4 | 522 | 2025-03
2025-03-02 18:00 | flat_start_nr | 136.97 | 4 | 550 | 2025-03
2025-03-02 19:00 | flat_start_nr | 139.25 | 5 | 546 | 2025-03
2025-03-02 20:00 | flat_start_nr | 142.77 | 5 | 547 | 2025-03
2025-03-02 21:00 | flat_start_nr | 143.49 | 4 | 542 | 2025-03
2025-03-02 22:00 | flat_start_nr | 149.11 | 5 | 539 | 2025-03
2025-03-02 23:00 | flat_start_nr | 141.26 | 4 | 544 | 2025-03
2025-03-03 | flat_start_nr | 142.72 | 4 | 544 | 2025-03
2025-03-03 01:00 | flat_start_nr | 140.17 | 5 | 544 | 2025-03
2025-03-03 02:00 | flat_start_nr | 135.67 | 5 | 541 | 2025-03
2025-03-03 03:00 | flat_start_nr | 135.31 | 5 | 538 | 2025-03
2025-03-03 04:00 | flat_start_nr | 129.08 | 4 | 538 | 2025-03
2025-03-03 05:00 | flat_start_nr | 127.8 | 3 | 534 | 2025-03
2025-03-03 06:00 | flat_start_nr | 125.3 | 3 | 539 | 2025-03
2025-03-03 07:00 | flat_start_nr | 135.92 | 4 | 533 | 2025-03
2025-03-03 08:00 | flat_start_nr | 140.05 | 4 | 543 | 2025-03
2025-03-03 09:00 | flat_start_nr | 143.2 | 4 | 532 | 2025-03
2025-03-03 10:00 | flat_start_nr | 143.81 | 4 | 524 | 2025-03
2025-03-03 11:00 | flat_start_nr | 146.97 | 5 | 523 | 2025-03
2025-03-03 12:00 | flat_start_nr | 148.03 | 5 | 525 | 2025-03
2025-03-03 13:00 | flat_start_nr | 146.59 | 5 | 525 | 2025-03
2025-03-03 14:00 | flat_start_nr | 143.92 | 4 | 531 | 2025-03
2025-03-03 16:00 | flat_start_nr | 139.16 | 4 | 524 | 2025-03
2025-03-03 17:00 | flat_start_nr | 135.82 | 4 | 533 | 2025-03
2025-03-03 18:00 | flat_start_nr | 121.12 | 3 | 533 | 2025-03
2025-03-03 19:00 | flat_start_nr | 118.57 | 4 | 531 | 2025-03
2025-03-03 20:00 | flat_start_nr | 116.93 | 2 | 536 | 2025-03
2025-03-03 21:00 | flat_start_nr | 119.09 | 3 | 532 | 2025-03
2025-03-03 22:00 | flat_start_nr | 118.3 | 3 | 532 | 2025-03
2025-03-03 23:00 | flat_start_nr | 118.82 | 3 | 535 | 2025-03
2025-03-04 | flat_start_nr | 117.08 | 3 | 541 | 2025-03
2025-03-04 01:00 | flat_start_nr | 122.41 | 3 | 532 | 2025-03
2025-03-04 02:00 | flat_start_nr | 121.35 | 3 | 533 | 2025-03
2025-03-04 03:00 | flat_start_nr | 116.42 | 2 | 548 | 2025-03
2025-03-04 04:00 | flat_start_nr | 116.45 | 2 | 543 | 2025-03
2025-03-04 05:00 | flat_start_nr | 116.53 | 2 | 544 | 2025-03
2025-03-04 06:00 | flat_start_nr | 119.2 | 2 | 550 | 2025-03
2025-03-04 07:00 | flat_start_nr | 142.18 | 3 | 550 | 2025-03
2025-03-04 08:00 | flat_start_nr | 141.96 | 4 | 534 | 2025-03
2025-03-04 09:00 | flat_start_nr | 151.24 | 6 | 536 | 2025-03
2025-03-04 12:00 | flat_start_nr | 150.15 | 5 | 524 | 2025-03
2025-03-04 13:00 | flat_start_nr | 149.77 | 5 | 533 | 2025-03
2025-03-04 17:00 | flat_start_nr | 143.07 | 4 | 535 | 2025-03
2025-03-04 18:00 | flat_start_nr | 128.31 | 4 | 532 | 2025-03
2025-03-04 19:00 | flat_start_nr | 124.04 | 4 | 542 | 2025-03
2025-03-04 20:00 | flat_start_nr | 125.98 | 4 | 544 | 2025-03
2025-03-04 21:00 | flat_start_nr | 130.39 | 5 | 545 | 2025-03
2025-03-04 22:00 | flat_start_nr | 136.34 | 5 | 557 | 2025-03
2025-03-04 23:00 | flat_start_nr | 130.06 | 5 | 547 | 2025-03
2025-03-05 | flat_start_nr | 132.88 | 6 | 545 | 2025-03
2025-03-05 01:00 | flat_start_nr | 131.36 | 6 | 542 | 2025-03
2025-03-05 02:00 | flat_start_nr | 132.87 | 5 | 539 | 2025-03
2025-03-05 03:00 | flat_start_nr | 125.38 | 3 | 542 | 2025-03
2025-03-05 04:00 | flat_start_nr | 116.29 | 2 | 541 | 2025-03
2025-03-05 05:00 | flat_start_nr | 116.2 | 2 | 542 | 2025-03
2025-03-05 06:00 | flat_start_nr | 116.03 | 2 | 542 | 2025-03
2025-03-05 07:00 | flat_start_nr | 118.66 | 4 | 543 | 2025-03
2025-03-05 08:00 | flat_start_nr | 122.81 | 3 | 543 | 2025-03
2025-03-05 09:00 | flat_start_nr | 133.39 | 4 | 532 | 2025-03
2025-03-05 10:00 | flat_start_nr | 144.13 | 4 | 526 | 2025-03
2025-03-05 11:00 | flat_start_nr | 150.85 | 6 | 521 | 2025-03
2025-03-05 13:00 | flat_start_nr | 150.97 | 6 | 533 | 2025-03
2025-03-05 14:00 | flat_start_nr | 152.81 | 6 | 535 | 2025-03
2025-03-05 15:00 | flat_start_nr | 147.68 | 5 | 516 | 2025-03
2025-03-05 16:00 | flat_start_nr | 124.06 | 3 | 542 | 2025-03
2025-03-05 17:00 | flat_start_nr | 120.92 | 3 | 541 | 2025-03
2025-03-05 18:00 | flat_start_nr | 111.32 | 2 | 545 | 2025-03
2025-03-05 19:00 | flat_start_nr | 110.27 | 1 | 554 | 2025-03
2025-03-05 20:00 | flat_start_nr | 123.33 | 2 | 556 | 2025-03
2025-03-05 21:00 | flat_start_nr | 114.76 | 2 | 546 | 2025-03
2025-03-05 22:00 | flat_start_nr | 116.16 | 3 | 546 | 2025-03
2025-03-05 23:00 | flat_start_nr | 117.82 | 4 | 542 | 2025-03
2025-03-06 | flat_start_nr | 116.64 | 3 | 546 | 2025-03
2025-03-06 01:00 | flat_start_nr | 121.54 | 4 | 534 | 2025-03
2025-03-06 02:00 | flat_start_nr | 129.12 | 4 | 546 | 2025-03
2025-03-06 03:00 | flat_start_nr | 126.77 | 4 | 545 | 2025-03
2025-03-06 04:00 | flat_start_nr | 125.94 | 4 | 544 | 2025-03
2025-03-06 05:00 | flat_start_nr | 125.33 | 4 | 544 | 2025-03
2025-03-06 06:00 | flat_start_nr | 116.62 | 3 | 546 | 2025-03
2025-03-06 07:00 | flat_start_nr | 131.56 | 5 | 539 | 2025-03
2025-03-06 08:00 | flat_start_nr | 139.15 | 4 | 547 | 2025-03
2025-03-06 09:00 | flat_start_nr | 141.36 | 4 | 548 | 2025-03
2025-03-06 10:00 | flat_start_nr | 148.68 | 4 | 534 | 2025-03
2025-03-06 11:00 | flat_start_nr | 151.33 | 5 | 523 | 2025-03
2025-03-06 12:00 | flat_start_nr | 143.46 | 3 | 542 | 2025-03
2025-03-06 13:00 | flat_start_nr | 131.44 | 3 | 553 | 2025-03
2025-03-06 14:00 | flat_start_nr | 128.67 | 3 | 544 | 2025-03
2025-03-06 15:00 | flat_start_nr | 137.41 | 4 | 537 | 2025-03
2025-03-06 16:00 | flat_start_nr | 137.56 | 4 | 542 | 2025-03
2025-03-06 17:00 | flat_start_nr | 131.75 | 4 | 552 | 2025-03
2025-03-06 18:00 | flat_start_nr | 125.53 | 2 | 551 | 2025-03
2025-03-06 19:00 | flat_start_nr | 112.11 | 2 | 550 | 2025-03
2025-03-06 20:00 | flat_start_nr | 113.57 | 3 | 551 | 2025-03
2025-03-06 21:00 | flat_start_nr | 116.29 | 3 | 548 | 2025-03
2025-03-06 22:00 | flat_start_nr | 130.34 | 4 | 539 | 2025-03
2025-03-06 23:00 | flat_start_nr | 141.09 | 5 | 548 | 2025-03
2025-03-07 | flat_start_nr | 141.96 | 5 | 552 | 2025-03
2025-03-07 01:00 | flat_start_nr | 148.11 | 6 | 539 | 2025-03
2025-03-07 02:00 | flat_start_nr | 147.29 | 6 | 534 | 2025-03
2025-03-07 03:00 | flat_start_nr | 150.56 | 6 | 536 | 2025-03
2025-03-07 04:00 | flat_start_nr | 151.04 | 6 | 537 | 2025-03
2025-03-07 05:00 | flat_start_nr | 136.22 | 5 | 548 | 2025-03
2025-03-07 06:00 | flat_start_nr | 126.33 | 4 | 546 | 2025-03
2025-03-07 07:00 | flat_start_nr | 133.56 | 4 | 535 | 2025-03
2025-03-07 08:00 | flat_start_nr | 137.79 | 4 | 544 | 2025-03
2025-03-07 09:00 | flat_start_nr | 146.22 | 4 | 543 | 2025-03
2025-03-07 10:00 | flat_start_nr | 139 | 4 | 545 | 2025-03
2025-03-07 11:00 | flat_start_nr | 135.93 | 4 | 543 | 2025-03
2025-03-07 12:00 | flat_start_nr | 135.07 | 4 | 533 | 2025-03
2025-03-07 13:00 | flat_start_nr | 140.68 | 4 | 543 | 2025-03
2025-03-07 14:00 | flat_start_nr | 144.14 | 4 | 536 | 2025-03
2025-03-07 15:00 | flat_start_nr | 147.82 | 5 | 534 | 2025-03
2025-03-07 16:00 | flat_start_nr | 149.97 | 6 | 520 | 2025-03
2025-03-07 17:00 | flat_start_nr | 135.29 | 4 | 544 | 2025-03
2025-03-07 18:00 | flat_start_nr | 121.26 | 3 | 544 | 2025-03
2025-03-07 19:00 | flat_start_nr | 121.02 | 3 | 546 | 2025-03
2025-03-07 20:00 | flat_start_nr | 129.59 | 4 | 526 | 2025-03
2025-03-07 21:00 | flat_start_nr | 141.39 | 4 | 534 | 2025-03
2025-03-07 22:00 | flat_start_nr | 157.58 | 6 | 532 | 2025-03
2025-03-08 02:00 | flat_start_nr | 153.54 | 6 | 506 | 2025-03
2025-03-08 03:00 | flat_start_nr | 146.02 | 6 | 520 | 2025-03
2025-03-08 04:00 | flat_start_nr | 149.54 | 6 | 515 | 2025-03
2025-03-08 05:00 | flat_start_nr | 139.65 | 4 | 528 | 2025-03
2025-03-08 06:00 | flat_start_nr | 138.87 | 4 | 529 | 2025-03
2025-03-08 07:00 | flat_start_nr | 155.97 | 6 | 524 | 2025-03
2025-03-08 18:00 | flat_start_nr | 142.33 | 4 | 523 | 2025-03
2025-03-08 19:00 | flat_start_nr | 129.33 | 3 | 524 | 2025-03
2025-03-08 20:00 | flat_start_nr | 133.52 | 4 | 524 | 2025-03
2025-03-08 21:00 | flat_start_nr | 136.11 | 4 | 524 | 2025-03
2025-03-08 22:00 | flat_start_nr | 137.74 | 5 | 522 | 2025-03
2025-03-08 23:00 | flat_start_nr | 139.69 | 4 | 524 | 2025-03
2025-03-09 | flat_start_nr | 145.69 | 5 | 518 | 2025-03
2025-03-09 01:00 | flat_start_nr | 147.25 | 5 | 516 | 2025-03
2025-03-09 02:00 | flat_start_nr | 151.1 | 5 | 514 | 2025-03
2025-03-09 03:00 | flat_start_nr | 156.92 | 6 | 529 | 2025-03
2025-03-09 04:00 | flat_start_nr | 155.77 | 6 | 509 | 2025-03
2025-03-09 17:00 | flat_start_nr | 153.5 | 5 | 509 | 2025-03
2025-03-09 18:00 | flat_start_nr | 137.33 | 4 | 527 | 2025-03
2025-03-09 19:00 | flat_start_nr | 127.68 | 3 | 525 | 2025-03
2025-03-09 20:00 | flat_start_nr | 129.4 | 3 | 524 | 2025-03
2025-03-09 21:00 | flat_start_nr | 135.53 | 5 | 526 | 2025-03
2025-03-09 22:00 | flat_start_nr | 135.96 | 5 | 529 | 2025-03
2025-03-09 23:00 | flat_start_nr | 143.65 | 4 | 535 | 2025-03
2025-03-10 | flat_start_nr | 157.03 | 6 | 548 | 2025-03
2025-03-10 01:00 | flat_start_nr | 156.9 | 6 | 543 | 2025-03
2025-03-10 02:00 | flat_start_nr | 151.53 | 5 | 530 | 2025-03
2025-03-10 03:00 | flat_start_nr | 148.19 | 5 | 538 | 2025-03
2025-03-10 04:00 | flat_start_nr | 136.2 | 3 | 545 | 2025-03
2025-03-10 05:00 | flat_start_nr | 136.99 | 4 | 539 | 2025-03
2025-03-10 06:00 | flat_start_nr | 132.2 | 4 | 541 | 2025-03
2025-03-10 07:00 | flat_start_nr | 136.1 | 3 | 536 | 2025-03
2025-03-10 08:00 | flat_start_nr | 137.21 | 3 | 542 | 2025-03
2025-03-10 09:00 | flat_start_nr | 131.42 | 3 | 537 | 2025-03
2025-03-10 10:00 | flat_start_nr | 130.36 | 3 | 550 | 2025-03
2025-03-10 11:00 | flat_start_nr | 132.71 | 3 | 544 | 2025-03
2025-03-10 12:00 | flat_start_nr | 131.87 | 3 | 540 | 2025-03
2025-03-10 13:00 | flat_start_nr | 135.15 | 3 | 540 | 2025-03
2025-03-10 14:00 | flat_start_nr | 146.79 | 4 | 529 | 2025-03
2025-03-10 15:00 | flat_start_nr | 155.83 | 5 | 536 | 2025-03
2025-03-10 18:00 | flat_start_nr | 143.22 | 3 | 533 | 2025-03
2025-03-10 19:00 | flat_start_nr | 126.44 | 3 | 531 | 2025-03
2025-03-10 20:00 | flat_start_nr | 125.41 | 3 | 535 | 2025-03
2025-03-10 21:00 | flat_start_nr | 121.57 | 4 | 538 | 2025-03
2025-03-10 22:00 | flat_start_nr | 127.43 | 4 | 542 | 2025-03
2025-03-10 23:00 | flat_start_nr | 138.91 | 5 | 539 | 2025-03
2025-03-11 | flat_start_nr | 132.34 | 5 | 541 | 2025-03
2025-03-11 01:00 | flat_start_nr | 139.07 | 5 | 548 | 2025-03
2025-03-11 02:00 | flat_start_nr | 138.21 | 4 | 544 | 2025-03
2025-03-11 03:00 | flat_start_nr | 134.31 | 4 | 541 | 2025-03
2025-03-11 04:00 | flat_start_nr | 119.58 | 3 | 547 | 2025-03
2025-03-11 05:00 | flat_start_nr | 111.72 | 2 | 549 | 2025-03
2025-03-11 06:00 | flat_start_nr | 111.73 | 2 | 554 | 2025-03
2025-03-11 07:00 | flat_start_nr | 125.11 | 3 | 539 | 2025-03
2025-03-11 08:00 | flat_start_nr | 151.66 | 5 | 528 | 2025-03
2025-03-11 10:00 | flat_start_nr | 156.14 | 5 | 538 | 2025-03
2025-03-11 11:00 | flat_start_nr | 141.38 | 3 | 536 | 2025-03
2025-03-11 12:00 | flat_start_nr | 135.01 | 4 | 533 | 2025-03
2025-03-11 13:00 | flat_start_nr | 139.02 | 4 | 535 | 2025-03
2025-03-11 14:00 | flat_start_nr | 140.99 | 4 | 543 | 2025-03
2025-03-11 15:00 | flat_start_nr | 140.7 | 4 | 542 | 2025-03
2025-03-11 16:00 | flat_start_nr | 139.25 | 4 | 533 | 2025-03
2025-03-11 17:00 | flat_start_nr | 140.58 | 4 | 548 | 2025-03
2025-03-11 18:00 | flat_start_nr | 123.43 | 4 | 542 | 2025-03
2025-03-11 19:00 | flat_start_nr | 109.63 | 2 | 542 | 2025-03
2025-03-11 20:00 | flat_start_nr | 112.98 | 2 | 529 | 2025-03
2025-03-11 21:00 | flat_start_nr | 121.63 | 4 | 538 | 2025-03
2025-03-11 22:00 | flat_start_nr | 126.98 | 4 | 538 | 2025-03
2025-03-11 23:00 | flat_start_nr | 113.04 | 3 | 543 | 2025-03
2025-03-12 | flat_start_nr | 111.21 | 1 | 546 | 2025-03
2025-03-12 01:00 | flat_start_nr | 109.96 | 2 | 544 | 2025-03
2025-03-12 02:00 | flat_start_nr | 110.1 | 2 | 545 | 2025-03
2025-03-12 03:00 | flat_start_nr | 111.84 | 2 | 545 | 2025-03
2025-03-12 04:00 | flat_start_nr | 112.17 | 2 | 546 | 2025-03
2025-03-12 05:00 | flat_start_nr | 118.32 | 2 | 558 | 2025-03
2025-03-12 06:00 | flat_start_nr | 119.96 | 2 | 563 | 2025-03
2025-03-12 07:00 | flat_start_nr | 140.76 | 3 | 563 | 2025-03
2025-03-12 08:00 | flat_start_nr | 136.33 | 4 | 554 | 2025-03
2025-03-12 09:00 | flat_start_nr | 139.65 | 4 | 542 | 2025-03
2025-03-12 10:00 | flat_start_nr | 134.54 | 4 | 529 | 2025-03
2025-03-12 11:00 | flat_start_nr | 137.52 | 4 | 533 | 2025-03
2025-03-12 12:00 | flat_start_nr | 135.84 | 4 | 533 | 2025-03
2025-03-12 13:00 | flat_start_nr | 138.31 | 4 | 535 | 2025-03
2025-03-12 14:00 | flat_start_nr | 138.48 | 4 | 534 | 2025-03
2025-03-12 15:00 | flat_start_nr | 138.42 | 4 | 534 | 2025-03
2025-03-12 16:00 | flat_start_nr | 138.75 | 4 | 550 | 2025-03
2025-03-12 17:00 | flat_start_nr | 138.24 | 4 | 538 | 2025-03
2025-03-12 18:00 | flat_start_nr | 134.84 | 4 | 533 | 2025-03
2025-03-12 19:00 | flat_start_nr | 127.81 | 3 | 549 | 2025-03
2025-03-12 20:00 | flat_start_nr | 123.48 | 3 | 553 | 2025-03
2025-03-12 21:00 | flat_start_nr | 125.34 | 3 | 552 | 2025-03
2025-03-12 22:00 | flat_start_nr | 136.15 | 4 | 555 | 2025-03
2025-03-12 23:00 | flat_start_nr | 138.22 | 4 | 563 | 2025-03
2025-03-13 | flat_start_nr | 138.33 | 4 | 556 | 2025-03
2025-03-13 01:00 | flat_start_nr | 144.99 | 4 | 553 | 2025-03
2025-03-13 02:00 | flat_start_nr | 136.06 | 4 | 556 | 2025-03
2025-03-13 03:00 | flat_start_nr | 133.15 | 4 | 547 | 2025-03
2025-03-13 04:00 | flat_start_nr | 121.92 | 3 | 543 | 2025-03
2025-03-13 05:00 | flat_start_nr | 114.09 | 3 | 544 | 2025-03
2025-03-13 06:00 | flat_start_nr | 109.38 | 3 | 538 | 2025-03
2025-03-13 07:00 | flat_start_nr | 111.62 | 3 | 534 | 2025-03
2025-03-13 08:00 | flat_start_nr | 118.55 | 3 | 529 | 2025-03
2025-03-13 09:00 | flat_start_nr | 130.16 | 4 | 538 | 2025-03
2025-03-13 10:00 | flat_start_nr | 123.59 | 3 | 543 | 2025-03
2025-03-13 11:00 | flat_start_nr | 117.71 | 3 | 542 | 2025-03
2025-03-13 12:00 | flat_start_nr | 112.26 | 2 | 543 | 2025-03
2025-03-13 13:00 | flat_start_nr | 115.05 | 2 | 541 | 2025-03
2025-03-13 14:00 | flat_start_nr | 137.75 | 4 | 539 | 2025-03
2025-03-13 17:00 | flat_start_nr | 144.72 | 4 | 528 | 2025-03
2025-03-13 18:00 | flat_start_nr | 142.59 | 5 | 533 | 2025-03
2025-03-13 19:00 | flat_start_nr | 133.84 | 3 | 540 | 2025-03
2025-03-13 20:00 | flat_start_nr | 121.02 | 4 | 536 | 2025-03
2025-03-13 21:00 | flat_start_nr | 116.63 | 4 | 533 | 2025-03
2025-03-13 22:00 | flat_start_nr | 113.55 | 3 | 532 | 2025-03
2025-03-13 23:00 | flat_start_nr | 113.26 | 3 | 532 | 2025-03
2025-03-14 | flat_start_nr | 114.71 | 3 | 532 | 2025-03
2025-03-14 01:00 | flat_start_nr | 122.55 | 3 | 536 | 2025-03
2025-03-14 02:00 | flat_start_nr | 123.26 | 3 | 538 | 2025-03
2025-03-14 03:00 | flat_start_nr | 113.99 | 2 | 534 | 2025-03
2025-03-14 04:00 | flat_start_nr | 113.14 | 2 | 536 | 2025-03
2025-03-14 05:00 | flat_start_nr | 112.7 | 2 | 545 | 2025-03
2025-03-14 06:00 | flat_start_nr | 109.73 | 2 | 546 | 2025-03
2025-03-14 07:00 | flat_start_nr | 124.29 | 3 | 536 | 2025-03
2025-03-14 08:00 | flat_start_nr | 127.6 | 3 | 528 | 2025-03
2025-03-14 09:00 | flat_start_nr | 150.17 | 6 | 527 | 2025-03
2025-03-14 12:00 | flat_start_nr | 152.24 | 6 | 548 | 2025-03
2025-03-14 13:00 | flat_start_nr | 151 | 6 | 523 | 2025-03
2025-03-14 14:00 | flat_start_nr | 152.12 | 6 | 524 | 2025-03
2025-03-14 15:00 | flat_start_nr | 152.75 | 6 | 529 | 2025-03
2025-03-14 17:00 | flat_start_nr | 142.72 | 4 | 535 | 2025-03
2025-03-14 18:00 | flat_start_nr | 140.1 | 4 | 544 | 2025-03
2025-03-14 19:00 | flat_start_nr | 129.7 | 4 | 545 | 2025-03
2025-03-14 20:00 | flat_start_nr | 123.65 | 3 | 549 | 2025-03
2025-03-14 21:00 | flat_start_nr | 117.34 | 3 | 550 | 2025-03
2025-03-14 22:00 | flat_start_nr | 122 | 3 | 551 | 2025-03
2025-03-14 23:00 | flat_start_nr | 123.69 | 3 | 545 | 2025-03
2025-03-15 | flat_start_nr | 123.55 | 3 | 536 | 2025-03
2025-03-15 01:00 | flat_start_nr | 125.48 | 3 | 535 | 2025-03
2025-03-15 02:00 | flat_start_nr | 122.27 | 3 | 538 | 2025-03
2025-03-15 03:00 | flat_start_nr | 120.99 | 3 | 537 | 2025-03
2025-03-15 04:00 | flat_start_nr | 125.26 | 3 | 535 | 2025-03
2025-03-15 05:00 | flat_start_nr | 126.06 | 3 | 535 | 2025-03
2025-03-15 06:00 | flat_start_nr | 135 | 3 | 543 | 2025-03
2025-03-15 09:00 | flat_start_nr | 141.32 | 4 | 525 | 2025-03
2025-03-15 10:00 | flat_start_nr | 139.99 | 4 | 531 | 2025-03
2025-03-15 11:00 | flat_start_nr | 141.73 | 4 | 525 | 2025-03
2025-03-15 12:00 | flat_start_nr | 145.78 | 5 | 509 | 2025-03
2025-03-15 13:00 | flat_start_nr | 151.24 | 6 | 511 | 2025-03
2025-03-15 14:00 | flat_start_nr | 150.59 | 6 | 512 | 2025-03
2025-03-15 15:00 | flat_start_nr | 149.65 | 6 | 514 | 2025-03
2025-03-15 18:00 | flat_start_nr | 140.9 | 3 | 547 | 2025-03
2025-03-15 19:00 | flat_start_nr | 130.23 | 4 | 538 | 2025-03
2025-03-15 20:00 | flat_start_nr | 133.36 | 4 | 540 | 2025-03
2025-03-15 21:00 | flat_start_nr | 131.91 | 4 | 543 | 2025-03
2025-03-15 22:00 | flat_start_nr | 122.2 | 3 | 530 | 2025-03
2025-03-15 23:00 | flat_start_nr | 122.24 | 3 | 533 | 2025-03
2025-03-16 | flat_start_nr | 122.95 | 3 | 529 | 2025-03
2025-03-16 01:00 | flat_start_nr | 124.39 | 3 | 534 | 2025-03
2025-03-16 02:00 | flat_start_nr | 125.57 | 3 | 534 | 2025-03
2025-03-16 03:00 | flat_start_nr | 123.01 | 3 | 535 | 2025-03
2025-03-16 04:00 | flat_start_nr | 125.37 | 3 | 533 | 2025-03
2025-03-16 05:00 | flat_start_nr | 119.87 | 3 | 533 | 2025-03
2025-03-16 06:00 | flat_start_nr | 119.12 | 3 | 533 | 2025-03
2025-03-16 07:00 | flat_start_nr | 130.46 | 4 | 531 | 2025-03
2025-03-16 08:00 | flat_start_nr | 131.15 | 4 | 531 | 2025-03
2025-03-16 09:00 | flat_start_nr | 132.14 | 4 | 540 | 2025-03
2025-03-16 10:00 | flat_start_nr | 131.37 | 4 | 539 | 2025-03
2025-03-16 11:00 | flat_start_nr | 134.15 | 4 | 540 | 2025-03
2025-03-16 12:00 | flat_start_nr | 133.05 | 4 | 540 | 2025-03
2025-03-16 13:00 | flat_start_nr | 134.46 | 4 | 543 | 2025-03
2025-03-16 14:00 | flat_start_nr | 140.96 | 4 | 525 | 2025-03
2025-03-16 15:00 | flat_start_nr | 140.29 | 4 | 535 | 2025-03
2025-03-16 16:00 | flat_start_nr | 138.66 | 4 | 538 | 2025-03
2025-03-16 17:00 | flat_start_nr | 136.96 | 4 | 537 | 2025-03
2025-03-16 18:00 | flat_start_nr | 124.13 | 3 | 536 | 2025-03
2025-03-16 19:00 | flat_start_nr | 121.25 | 3 | 538 | 2025-03
2025-03-16 20:00 | flat_start_nr | 121.77 | 3 | 539 | 2025-03
2025-03-16 21:00 | flat_start_nr | 123.11 | 3 | 537 | 2025-03
2025-03-16 22:00 | flat_start_nr | 115.31 | 2 | 541 | 2025-03
2025-03-16 23:00 | flat_start_nr | 120.05 | 3 | 541 | 2025-03
2025-03-17 | flat_start_nr | 121.72 | 3 | 538 | 2025-03
2025-03-17 01:00 | flat_start_nr | 119.53 | 3 | 534 | 2025-03
2025-03-17 02:00 | flat_start_nr | 117.8 | 3 | 532 | 2025-03
2025-03-17 03:00 | flat_start_nr | 117.42 | 3 | 531 | 2025-03
2025-03-17 04:00 | flat_start_nr | 118.49 | 3 | 531 | 2025-03
2025-03-17 05:00 | flat_start_nr | 117.67 | 3 | 531 | 2025-03
2025-03-17 06:00 | flat_start_nr | 126.35 | 2 | 542 | 2025-03
2025-03-17 07:00 | flat_start_nr | 140.58 | 3 | 542 | 2025-03
2025-03-17 08:00 | flat_start_nr | 135.24 | 4 | 535 | 2025-03
2025-03-17 09:00 | flat_start_nr | 132.18 | 4 | 530 | 2025-03
2025-03-17 10:00 | flat_start_nr | 141.98 | 4 | 523 | 2025-03
2025-03-17 11:00 | flat_start_nr | 153.8 | 6 | 537 | 2025-03
2025-03-17 15:00 | flat_start_nr | 153 | 6 | 525 | 2025-03
2025-03-17 18:00 | flat_start_nr | 142.06 | 5 | 513 | 2025-03
2025-03-17 19:00 | flat_start_nr | 139 | 3 | 538 | 2025-03
2025-03-17 20:00 | flat_start_nr | 127.54 | 3 | 531 | 2025-03
2025-03-17 21:00 | flat_start_nr | 139.02 | 4 | 540 | 2025-03
2025-03-17 22:00 | flat_start_nr | 143.43 | 4 | 544 | 2025-03
2025-03-17 23:00 | flat_start_nr | 144.04 | 4 | 538 | 2025-03
2025-03-18 | flat_start_nr | 144.7 | 4 | 541 | 2025-03
2025-03-18 01:00 | flat_start_nr | 143.24 | 4 | 542 | 2025-03
2025-03-18 02:00 | flat_start_nr | 155.22 | 5 | 524 | 2025-03
2025-03-18 03:00 | flat_start_nr | 154.37 | 5 | 530 | 2025-03
2025-03-18 04:00 | flat_start_nr | 155.78 | 5 | 550 | 2025-03
2025-03-18 05:00 | flat_start_nr | 139.5 | 4 | 536 | 2025-03
2025-03-18 06:00 | flat_start_nr | 128.21 | 3 | 529 | 2025-03
2025-03-18 07:00 | flat_start_nr | 143.16 | 4 | 533 | 2025-03
2025-03-18 08:00 | flat_start_nr | 142.86 | 4 | 533 | 2025-03
2025-03-18 09:00 | flat_start_nr | 151.13 | 6 | 519 | 2025-03
2025-03-18 10:00 | flat_start_nr | 148.75 | 5 | 518 | 2025-03
2025-03-18 11:00 | flat_start_nr | 145.45 | 4 | 529 | 2025-03
2025-03-18 12:00 | flat_start_nr | 143.78 | 4 | 524 | 2025-03
2025-03-18 13:00 | flat_start_nr | 143.47 | 4 | 537 | 2025-03
2025-03-18 14:00 | flat_start_nr | 141.59 | 5 | 539 | 2025-03
2025-03-18 15:00 | flat_start_nr | 143.42 | 4 | 530 | 2025-03
2025-03-18 17:00 | flat_start_nr | 136.03 | 5 | 531 | 2025-03
2025-03-18 18:00 | flat_start_nr | 140.76 | 5 | 525 | 2025-03
2025-03-18 19:00 | flat_start_nr | 141.49 | 4 | 548 | 2025-03
2025-03-19 03:00 | flat_start_nr | 153.32 | 6 | 534 | 2025-03
2025-03-19 04:00 | flat_start_nr | 138.07 | 4 | 542 | 2025-03
2025-03-19 05:00 | flat_start_nr | 132.27 | 5 | 548 | 2025-03
2025-03-19 06:00 | flat_start_nr | 142.56 | 4 | 539 | 2025-03
2025-03-19 07:00 | flat_start_nr | 136.42 | 4 | 535 | 2025-03
2025-03-19 08:00 | flat_start_nr | 138.12 | 4 | 545 | 2025-03
2025-03-19 09:00 | flat_start_nr | 138.88 | 4 | 545 | 2025-03
2025-03-19 10:00 | flat_start_nr | 136.46 | 4 | 544 | 2025-03
2025-03-19 11:00 | flat_start_nr | 143.13 | 4 | 548 | 2025-03
2025-03-19 12:00 | flat_start_nr | 151.09 | 5 | 529 | 2025-03
2025-03-19 15:00 | flat_start_nr | 153.77 | 5 | 534 | 2025-03
2025-03-19 16:00 | flat_start_nr | 150.44 | 6 | 527 | 2025-03
2025-03-19 18:00 | flat_start_nr | 150.82 | 7 | 516 | 2025-03
2025-03-19 19:00 | flat_start_nr | 131.89 | 5 | 543 | 2025-03
2025-03-19 20:00 | flat_start_nr | 128.16 | 4 | 545 | 2025-03
2025-03-19 21:00 | flat_start_nr | 135.09 | 5 | 542 | 2025-03
2025-03-19 22:00 | flat_start_nr | 155.53 | 6 | 525 | 2025-03
2025-03-20 | normal_nr | 158.71 | 6 | 537 | 2025-03
2025-03-20 01:00 | flat_start_nr | 153.18 | 6 | 528 | 2025-03
2025-03-20 02:00 | flat_start_nr | 148.83 | 5 | 528 | 2025-03
2025-03-20 03:00 | flat_start_nr | 147.68 | 5 | 539 | 2025-03
2025-03-20 04:00 | flat_start_nr | 145.53 | 5 | 541 | 2025-03
2025-03-20 05:00 | flat_start_nr | 140.23 | 4 | 539 | 2025-03
2025-03-20 06:00 | flat_start_nr | 145.44 | 7 | 536 | 2025-03
2025-03-20 07:00 | flat_start_nr | 152.39 | 7 | 523 | 2025-03
2025-03-20 08:00 | flat_start_nr | 152.37 | 8 | 529 | 2025-03
2025-03-20 09:00 | flat_start_nr | 151.88 | 8 | 530 | 2025-03
2025-03-20 10:00 | flat_start_nr | 152.31 | 7 | 528 | 2025-03
2025-03-20 11:00 | flat_start_nr | 151.95 | 6 | 522 | 2025-03
2025-03-20 12:00 | flat_start_nr | 150.51 | 6 | 515 | 2025-03
2025-03-20 13:00 | flat_start_nr | 150.75 | 6 | 517 | 2025-03
2025-03-20 14:00 | flat_start_nr | 151.22 | 6 | 518 | 2025-03
2025-03-20 16:00 | flat_start_nr | 152.53 | 6 | 520 | 2025-03
2025-03-20 19:00 | flat_start_nr | 135.95 | 4 | 537 | 2025-03
2025-03-20 20:00 | flat_start_nr | 133.96 | 4 | 538 | 2025-03
2025-03-20 21:00 | flat_start_nr | 129.42 | 4 | 539 | 2025-03
2025-03-20 22:00 | flat_start_nr | 144.23 | 5 | 540 | 2025-03
2025-03-20 23:00 | flat_start_nr | 145.62 | 6 | 538 | 2025-03
2025-03-21 | flat_start_nr | 148.25 | 5 | 530 | 2025-03
2025-03-21 01:00 | flat_start_nr | 157.67 | 7 | 543 | 2025-03
2025-03-21 03:00 | flat_start_nr | 153.67 | 7 | 520 | 2025-03
2025-03-21 04:00 | flat_start_nr | 135.18 | 6 | 544 | 2025-03
2025-03-21 05:00 | flat_start_nr | 127.67 | 5 | 547 | 2025-03
2025-03-21 06:00 | flat_start_nr | 138.35 | 5 | 537 | 2025-03
2025-03-21 07:00 | flat_start_nr | 150.05 | 6 | 530 | 2025-03
2025-03-21 08:00 | flat_start_nr | 154.28 | 6 | 555 | 2025-03
2025-03-21 19:00 | flat_start_nr | 136.09 | 5 | 547 | 2025-03
2025-03-21 20:00 | flat_start_nr | 136.79 | 6 | 547 | 2025-03
2025-03-21 21:00 | flat_start_nr | 155.07 | 8 | 532 | 2025-03
2025-03-21 22:00 | flat_start_nr | 148.25 | 7 | 546 | 2025-03
2025-03-22 01:00 | flat_start_nr | 151.28 | 5 | 528 | 2025-03
2025-03-22 02:00 | flat_start_nr | 145.79 | 5 | 544 | 2025-03
2025-03-22 03:00 | flat_start_nr | 146.35 | 5 | 541 | 2025-03
2025-03-22 04:00 | flat_start_nr | 141.69 | 4 | 546 | 2025-03
2025-03-22 05:00 | flat_start_nr | 155.91 | 6 | 532 | 2025-03
2025-03-22 18:00 | flat_start_nr | 147.67 | 5 | 526 | 2025-03
2025-03-22 19:00 | flat_start_nr | 137 | 4 | 543 | 2025-03
2025-03-22 20:00 | flat_start_nr | 134.99 | 4 | 546 | 2025-03
2025-03-22 21:00 | flat_start_nr | 142.46 | 4 | 554 | 2025-03
2025-03-22 22:00 | flat_start_nr | 151.77 | 4 | 534 | 2025-03
2025-03-23 04:00 | flat_start_nr | 155.6 | 6 | 522 | 2025-03
2025-03-23 05:00 | flat_start_nr | 130.59 | 4 | 544 | 2025-03
2025-03-23 06:00 | flat_start_nr | 141.8 | 4 | 537 | 2025-03
2025-03-23 07:00 | flat_start_nr | 153.9 | 6 | 536 | 2025-03
2025-03-23 16:00 | flat_start_nr | 152.98 | 6 | 544 | 2025-03
2025-03-23 17:00 | flat_start_nr | 151.81 | 6 | 524 | 2025-03
2025-03-23 18:00 | flat_start_nr | 132.74 | 4 | 545 | 2025-03
2025-03-23 19:00 | flat_start_nr | 126.7 | 3 | 541 | 2025-03
2025-03-23 20:00 | flat_start_nr | 133.68 | 4 | 546 | 2025-03
2025-03-23 21:00 | flat_start_nr | 135.18 | 4 | 552 | 2025-03
2025-03-23 22:00 | flat_start_nr | 137.71 | 4 | 552 | 2025-03
2025-03-23 23:00 | flat_start_nr | 141.48 | 4 | 548 | 2025-03
2025-03-24 | flat_start_nr | 138.8 | 5 | 551 | 2025-03
2025-03-24 01:00 | flat_start_nr | 138.41 | 5 | 549 | 2025-03
2025-03-24 02:00 | flat_start_nr | 138.21 | 5 | 549 | 2025-03
2025-03-24 03:00 | flat_start_nr | 137.19 | 5 | 543 | 2025-03
2025-03-24 04:00 | flat_start_nr | 134.81 | 4 | 539 | 2025-03
2025-03-24 05:00 | flat_start_nr | 127.49 | 3 | 534 | 2025-03
2025-03-24 06:00 | flat_start_nr | 142.99 | 4 | 524 | 2025-03
2025-03-24 07:00 | flat_start_nr | 150.87 | 6 | 539 | 2025-03
2025-03-24 16:00 | flat_start_nr | 153.3 | 6 | 541 | 2025-03
2025-03-24 18:00 | flat_start_nr | 149.17 | 6 | 512 | 2025-03
2025-03-24 19:00 | flat_start_nr | 129.48 | 4 | 543 | 2025-03
2025-03-24 20:00 | flat_start_nr | 139.57 | 4 | 545 | 2025-03
2025-03-24 21:00 | flat_start_nr | 153.93 | 6 | 534 | 2025-03
2025-03-24 22:00 | flat_start_nr | 146.32 | 5 | 547 | 2025-03
2025-03-24 23:00 | flat_start_nr | 141.48 | 4 | 552 | 2025-03
2025-03-25 | flat_start_nr | 140.02 | 4 | 552 | 2025-03
2025-03-25 01:00 | flat_start_nr | 137.76 | 4 | 552 | 2025-03
2025-03-25 02:00 | flat_start_nr | 134.54 | 4 | 545 | 2025-03
2025-03-25 03:00 | flat_start_nr | 133.02 | 4 | 548 | 2025-03
2025-03-25 04:00 | flat_start_nr | 134.62 | 5 | 545 | 2025-03
2025-03-25 05:00 | flat_start_nr | 138.24 | 4 | 549 | 2025-03
2025-03-25 09:00 | flat_start_nr | 143.05 | 4 | 524 | 2025-03
2025-03-25 10:00 | flat_start_nr | 137.39 | 5 | 535 | 2025-03
2025-03-25 11:00 | flat_start_nr | 139.71 | 4 | 538 | 2025-03
2025-03-25 12:00 | flat_start_nr | 148.71 | 5 | 523 | 2025-03
2025-03-25 13:00 | flat_start_nr | 148.9 | 5 | 529 | 2025-03
2025-03-25 14:00 | flat_start_nr | 148.7 | 5 | 520 | 2025-03
2025-03-25 17:00 | flat_start_nr | 143.38 | 4 | 514 | 2025-03
2025-03-25 18:00 | flat_start_nr | 142.12 | 4 | 533 | 2025-03
2025-03-25 19:00 | flat_start_nr | 131.86 | 4 | 535 | 2025-03
2025-03-25 20:00 | flat_start_nr | 147.92 | 4 | 530 | 2025-03
2025-03-25 21:00 | flat_start_nr | 154.14 | 5 | 517 | 2025-03
2025-03-25 22:00 | flat_start_nr | 158.49 | 5 | 528 | 2025-03
2025-03-26 05:00 | flat_start_nr | 151.94 | 6 | 529 | 2025-03
2025-03-26 06:00 | flat_start_nr | 141.3 | 3 | 535 | 2025-03
2025-03-26 07:00 | flat_start_nr | 143.47 | 3 | 524 | 2025-03
2025-03-26 08:00 | flat_start_nr | 146.19 | 4 | 527 | 2025-03
2025-03-26 09:00 | flat_start_nr | 151.6 | 5 | 519 | 2025-03
2025-03-26 16:00 | flat_start_nr | 148.99 | 4 | 528 | 2025-03
2025-03-26 19:00 | flat_start_nr | 157.11 | 5 | 558 | 2025-03
2025-03-27 05:00 | flat_start_nr | 155.4 | 5 | 536 | 2025-03
2025-03-27 06:00 | flat_start_nr | 153.4 | 5 | 561 | 2025-03
2025-03-27 07:00 | flat_start_nr | 141.41 | 3 | 551 | 2025-03
2025-03-27 08:00 | flat_start_nr | 154.04 | 5 | 532 | 2025-03
2025-03-27 10:00 | flat_start_nr | 146.38 | 4 | 534 | 2025-03
2025-03-27 11:00 | flat_start_nr | 145.05 | 3 | 528 | 2025-03
2025-03-27 18:00 | flat_start_nr | 138.21 | 4 | 540 | 2025-03
2025-03-27 19:00 | flat_start_nr | 120.91 | 2 | 543 | 2025-03
2025-03-27 20:00 | flat_start_nr | 130.88 | 3 | 540 | 2025-03
2025-03-27 21:00 | flat_start_nr | 131.15 | 3 | 539 | 2025-03
2025-03-27 22:00 | flat_start_nr | 130.23 | 3 | 548 | 2025-03
2025-03-27 23:00 | flat_start_nr | 122.75 | 2 | 539 | 2025-03
2025-03-28 | flat_start_nr | 136.95 | 3 | 547 | 2025-03
2025-03-28 01:00 | flat_start_nr | 127.62 | 3 | 536 | 2025-03
2025-03-28 02:00 | flat_start_nr | 133.52 | 4 | 539 | 2025-03
2025-03-28 03:00 | flat_start_nr | 133.02 | 4 | 542 | 2025-03
2025-03-28 04:00 | flat_start_nr | 109.67 | 2 | 535 | 2025-03
2025-03-28 05:00 | flat_start_nr | 111.02 | 2 | 536 | 2025-03
2025-03-28 06:00 | flat_start_nr | 109.27 | 2 | 533 | 2025-03
2025-03-28 07:00 | flat_start_nr | 124.8 | 3 | 532 | 2025-03
2025-03-28 08:00 | flat_start_nr | 132.88 | 3 | 532 | 2025-03
2025-03-28 09:00 | flat_start_nr | 136.27 | 3 | 535 | 2025-03
2025-03-28 10:00 | flat_start_nr | 135.41 | 3 | 539 | 2025-03
2025-03-28 11:00 | flat_start_nr | 139.39 | 3 | 546 | 2025-03
2025-03-28 12:00 | flat_start_nr | 136.66 | 3 | 545 | 2025-03
2025-03-28 13:00 | flat_start_nr | 127.86 | 2 | 538 | 2025-03
2025-03-28 14:00 | flat_start_nr | 126.71 | 3 | 539 | 2025-03
2025-03-28 15:00 | flat_start_nr | 126.42 | 3 | 532 | 2025-03
2025-03-28 16:00 | flat_start_nr | 128.76 | 3 | 532 | 2025-03
2025-03-28 17:00 | flat_start_nr | 129.22 | 4 | 535 | 2025-03
2025-03-28 18:00 | flat_start_nr | 132.57 | 3 | 537 | 2025-03
2025-03-28 19:00 | flat_start_nr | 128 | 2 | 542 | 2025-03
2025-03-28 20:00 | flat_start_nr | 117.88 | 3 | 538 | 2025-03
2025-03-28 21:00 | flat_start_nr | 113.3 | 2 | 535 | 2025-03
2025-03-28 22:00 | flat_start_nr | 113 | 2 | 536 | 2025-03
2025-03-28 23:00 | flat_start_nr | 113.92 | 2 | 536 | 2025-03
2025-03-29 | flat_start_nr | 116.36 | 3 | 534 | 2025-03
2025-03-29 01:00 | flat_start_nr | 127.61 | 3 | 537 | 2025-03
2025-03-29 02:00 | flat_start_nr | 127.96 | 3 | 537 | 2025-03
2025-03-29 03:00 | flat_start_nr | 125.87 | 3 | 535 | 2025-03
2025-03-29 04:00 | flat_start_nr | 121.23 | 3 | 535 | 2025-03
2025-03-29 05:00 | flat_start_nr | 117.12 | 3 | 534 | 2025-03
2025-03-29 06:00 | flat_start_nr | 120.52 | 3 | 538 | 2025-03
2025-03-29 07:00 | flat_start_nr | 131.56 | 4 | 528 | 2025-03
2025-03-29 08:00 | flat_start_nr | 132.13 | 4 | 530 | 2025-03
2025-03-29 09:00 | flat_start_nr | 131.91 | 4 | 534 | 2025-03
2025-03-29 10:00 | flat_start_nr | 141.84 | 4 | 529 | 2025-03
2025-03-29 11:00 | flat_start_nr | 147.18 | 5 | 521 | 2025-03
2025-03-29 15:00 | flat_start_nr | 146.14 | 4 | 529 | 2025-03
2025-03-29 16:00 | flat_start_nr | 143.53 | 3 | 529 | 2025-03
2025-03-29 17:00 | flat_start_nr | 147.6 | 4 | 510 | 2025-03
2025-03-29 18:00 | flat_start_nr | 142.86 | 3 | 531 | 2025-03
2025-03-29 19:00 | flat_start_nr | 127.59 | 2 | 540 | 2025-03
2025-03-29 20:00 | flat_start_nr | 128.71 | 2 | 540 | 2025-03
2025-03-29 21:00 | flat_start_nr | 131.86 | 3 | 540 | 2025-03
2025-03-29 22:00 | flat_start_nr | 143.17 | 3 | 553 | 2025-03
2025-03-29 23:00 | flat_start_nr | 145.77 | 4 | 544 | 2025-03
2025-03-30 | flat_start_nr | 140.34 | 3 | 540 | 2025-03
2025-03-30 01:00 | flat_start_nr | 144.88 | 3 | 537 | 2025-03
2025-03-30 02:00 | flat_start_nr | 145.54 | 4 | 537 | 2025-03
2025-03-30 03:00 | flat_start_nr | 149.86 | 4 | 526 | 2025-03
2025-03-30 04:00 | flat_start_nr | 140.11 | 3 | 543 | 2025-03
2025-03-30 05:00 | flat_start_nr | 134.25 | 3 | 540 | 2025-03
2025-03-30 06:00 | flat_start_nr | 146.91 | 4 | 514 | 2025-03
2025-03-30 08:00 | flat_start_nr | 150.06 | 5 | 517 | 2025-03
2025-03-30 09:00 | flat_start_nr | 151.85 | 5 | 546 | 2025-03
2025-03-30 19:00 | flat_start_nr | 134.35 | 3 | 546 | 2025-03
2025-03-30 20:00 | flat_start_nr | 143.85 | 3 | 548 | 2025-03
2025-03-31 05:00 | flat_start_nr | 148.79 | 4 | 526 | 2025-03
2025-03-31 06:00 | flat_start_nr | 144.15 | 3 | 533 | 2025-03
2025-03-31 07:00 | flat_start_nr | 149.81 | 4 | 522 | 2025-03
2025-03-31 08:00 | flat_start_nr | 150.84 | 5 | 515 | 2025-03
2025-03-31 19:00 | flat_start_nr | 146.69 | 4 | 538 | 2025-03
2025-03-31 20:00 | flat_start_nr | 147.06 | 4 | 531 | 2025-03
2025-03-31 23:00 | flat_start_nr | 152.38 | 5 | 530 | 2025-03
2025-04-01 | flat_start_nr | 150.1 | 4 | 531 | 2025-04
2025-04-01 01:00 | flat_start_nr | 144.83 | 3 | 544 | 2025-04
2025-04-01 02:00 | flat_start_nr | 146.37 | 4 | 537 | 2025-04
2025-04-01 03:00 | flat_start_nr | 151.6 | 5 | 527 | 2025-04
2025-04-01 04:00 | flat_start_nr | 151.23 | 5 | 521 | 2025-04
2025-04-01 05:00 | flat_start_nr | 148.92 | 4 | 525 | 2025-04
2025-04-01 19:00 | flat_start_nr | 142.07 | 3 | 551 | 2025-04
2025-04-01 23:00 | flat_start_nr | 155.27 | 5 | 554 | 2025-04
2025-04-02 | flat_start_nr | 152.32 | 5 | 528 | 2025-04
2025-04-02 05:00 | flat_start_nr | 155.92 | 5 | 540 | 2025-04
2025-04-02 20:00 | flat_start_nr | 153.71 | 5 | 534 | 2025-04
2025-04-02 22:00 | flat_start_nr | 155.13 | 5 | 536 | 2025-04
2025-04-02 23:00 | normal_nr | 158.24 | 5 | 532 | 2025-04
2025-04-03 | flat_start_nr | 142.52 | 3 | 546 | 2025-04
2025-04-03 01:00 | flat_start_nr | 146.22 | 4 | 535 | 2025-04
2025-04-03 02:00 | flat_start_nr | 156.17 | 5 | 541 | 2025-04
2025-04-03 20:00 | flat_start_nr | 147.26 | 4 | 520 | 2025-04
2025-04-03 21:00 | flat_start_nr | 151.05 | 5 | 513 | 2025-04
2025-04-03 22:00 | flat_start_nr | 142.7 | 3 | 534 | 2025-04
2025-04-03 23:00 | flat_start_nr | 143.12 | 3 | 535 | 2025-04
2025-04-04 | flat_start_nr | 150.5 | 4 | 525 | 2025-04
2025-04-04 01:00 | flat_start_nr | 150.94 | 4 | 526 | 2025-04
2025-04-04 02:00 | flat_start_nr | 153.7 | 5 | 525 | 2025-04
2025-04-04 03:00 | flat_start_nr | 150.03 | 4 | 527 | 2025-04
2025-04-04 04:00 | flat_start_nr | 150.39 | 4 | 530 | 2025-04
2025-04-04 19:00 | flat_start_nr | 150.64 | 5 | 522 | 2025-04
2025-04-04 20:00 | flat_start_nr | 151.77 | 5 | 510 | 2025-04
2025-04-04 21:00 | flat_start_nr | 150.4 | 4 | 524 | 2025-04
2025-04-05 04:00 | flat_start_nr | 155.8 | 5 | 560 | 2025-04
2025-04-05 20:00 | flat_start_nr | 147.45 | 4 | 526 | 2025-04
2025-04-05 23:00 | flat_start_nr | 151.33 | 4 | 527 | 2025-04
2025-04-06 | flat_start_nr | 149.31 | 5 | 525 | 2025-04
2025-04-06 01:00 | flat_start_nr | 156.85 | 6 | 548 | 2025-04
2025-04-06 04:00 | flat_start_nr | 157.13 | 5 | 536 | 2025-04
2025-04-06 05:00 | flat_start_nr | 150.54 | 4 | 529 | 2025-04
2025-04-07 05:00 | flat_start_nr | 154.57 | 7 | 532 | 2025-04
2025-04-07 08:00 | flat_start_nr | 157.18 | 6 | 536 | 2025-04
2025-04-07 09:00 | flat_start_nr | 154.13 | 6 | 529 | 2025-04
2025-04-07 19:00 | flat_start_nr | 156.88 | 7 | 558 | 2025-04
2025-04-07 20:00 | normal_nr | 161.19 | 7 | 553 | 2025-04
2025-04-07 23:00 | flat_start_nr | 151.18 | 5 | 536 | 2025-04
2025-04-08 | flat_start_nr | 156.07 | 6 | 529 | 2025-04
2025-04-08 01:00 | flat_start_nr | 157.48 | 6 | 548 | 2025-04
2025-04-08 02:00 | flat_start_nr | 156.01 | 6 | 529 | 2025-04
2025-04-08 03:00 | flat_start_nr | 148.44 | 5 | 534 | 2025-04
2025-04-08 04:00 | flat_start_nr | 154.32 | 6 | 526 | 2025-04
2025-04-08 05:00 | flat_start_nr | 141.65 | 5 | 545 | 2025-04
2025-04-08 10:00 | flat_start_nr | 158.46 | 7 | 536 | 2025-04
2025-04-08 20:00 | flat_start_nr | 138.69 | 3 | 542 | 2025-04
2025-04-08 21:00 | flat_start_nr | 140.48 | 3 | 542 | 2025-04
2025-04-08 22:00 | flat_start_nr | 145.86 | 5 | 541 | 2025-04
2025-04-08 23:00 | flat_start_nr | 144.67 | 4 | 548 | 2025-04
2025-04-09 | flat_start_nr | 145.22 | 3 | 544 | 2025-04
2025-04-09 01:00 | flat_start_nr | 158.52 | 5 | 545 | 2025-04
2025-04-09 04:00 | flat_start_nr | 156.69 | 6 | 544 | 2025-04
2025-04-09 05:00 | flat_start_nr | 156.18 | 6 | 557 | 2025-04
2025-04-09 09:00 | normal_nr | 163.74 | 7 | 532 | 2025-04
2025-04-09 19:00 | flat_start_nr | 144.23 | 4 | 549 | 2025-04
2025-04-10 | flat_start_nr | 157.71 | 7 | 542 | 2025-04
2025-04-10 02:00 | normal_nr | 161.25 | 6 | 551 | 2025-04
2025-04-10 03:00 | flat_start_nr | 148.44 | 5 | 532 | 2025-04
2025-04-10 04:00 | flat_start_nr | 140.12 | 4 | 539 | 2025-04
2025-04-10 05:00 | flat_start_nr | 150.13 | 4 | 524 | 2025-04
2025-04-10 19:00 | flat_start_nr | 156.52 | 6 | 553 | 2025-04
2025-04-10 20:00 | flat_start_nr | 145.24 | 6 | 539 | 2025-04
2025-04-10 21:00 | flat_start_nr | 145.68 | 6 | 539 | 2025-04
2025-04-10 22:00 | flat_start_nr | 152.47 | 6 | 529 | 2025-04
2025-04-11 10:00 | normal_nr | 165.01 | 8 | 533 | 2025-04
2025-04-11 20:00 | flat_start_nr | 158.91 | 6 | 544 | 2025-04
2025-04-11 23:00 | flat_start_nr | 155.2 | 5 | 527 | 2025-04
2025-04-12 | flat_start_nr | 146.49 | 4 | 540 | 2025-04
2025-04-12 01:00 | flat_start_nr | 145.47 | 4 | 540 | 2025-04
2025-04-12 02:00 | flat_start_nr | 149.66 | 4 | 531 | 2025-04
2025-04-12 03:00 | flat_start_nr | 147.06 | 4 | 535 | 2025-04
2025-04-12 04:00 | flat_start_nr | 145.89 | 4 | 537 | 2025-04
2025-04-12 05:00 | flat_start_nr | 151.09 | 5 | 521 | 2025-04
2025-04-13 20:00 | flat_start_nr | 143.44 | 3 | 544 | 2025-04
2025-04-13 21:00 | flat_start_nr | 145.64 | 4 | 539 | 2025-04
2025-04-13 22:00 | flat_start_nr | 147.18 | 4 | 533 | 2025-04
2025-04-13 23:00 | flat_start_nr | 148.3 | 4 | 530 | 2025-04
2025-04-14 | flat_start_nr | 152.06 | 5 | 531 | 2025-04
2025-04-14 01:00 | flat_start_nr | 151.41 | 5 | 533 | 2025-04
2025-04-14 02:00 | flat_start_nr | 151.75 | 5 | 529 | 2025-04
2025-04-14 03:00 | flat_start_nr | 147.48 | 4 | 537 | 2025-04
2025-04-14 04:00 | flat_start_nr | 150.46 | 4 | 531 | 2025-04
2025-04-14 09:00 | flat_start_nr | 154.73 | 5 | 533 | 2025-04
2025-04-14 10:00 | flat_start_nr | 155.94 | 5 | 520 | 2025-04
2025-04-16 20:00 | flat_start_nr | 141.89 | 4 | 531 | 2025-04
2025-04-16 21:00 | flat_start_nr | 143.51 | 4 | 531 | 2025-04
2025-04-16 22:00 | flat_start_nr | 147.37 | 4 | 527 | 2025-04
2025-04-16 23:00 | flat_start_nr | 151.53 | 4 | 524 | 2025-04
2025-04-17 20:00 | flat_start_nr | 149.68 | 4 | 533 | 2025-04
2025-04-17 21:00 | flat_start_nr | 151.73 | 5 | 525 | 2025-04
2025-04-17 22:00 | flat_start_nr | 149.33 | 4 | 527 | 2025-04
2025-04-17 23:00 | flat_start_nr | 153.04 | 5 | 523 | 2025-04
2025-04-18 | flat_start_nr | 154.88 | 5 | 544 | 2025-04
2025-04-18 01:00 | flat_start_nr | 152.81 | 5 | 520 | 2025-04
2025-04-18 02:00 | flat_start_nr | 151.62 | 5 | 519 | 2025-04
2025-04-18 03:00 | flat_start_nr | 146.98 | 4 | 533 | 2025-04
2025-04-18 04:00 | flat_start_nr | 144.11 | 3 | 539 | 2025-04
2025-04-19 21:00 | flat_start_nr | 155.52 | 5 | 552 | 2025-04
2025-04-19 22:00 | flat_start_nr | 154.62 | 5 | 550 | 2025-04
2025-04-20 04:00 | flat_start_nr | 156.4 | 5 | 543 | 2025-04
2025-04-20 05:00 | flat_start_nr | 153.28 | 5 | 517 | 2025-04
2025-04-20 20:00 | flat_start_nr | 142.39 | 3 | 543 | 2025-04
2025-04-20 21:00 | flat_start_nr | 143.73 | 3 | 538 | 2025-04
2025-04-20 22:00 | flat_start_nr | 148.92 | 4 | 524 | 2025-04
2025-04-20 23:00 | flat_start_nr | 145.85 | 4 | 534 | 2025-04
2025-04-21 | flat_start_nr | 138.44 | 4 | 541 | 2025-04
2025-04-21 01:00 | flat_start_nr | 137.55 | 4 | 538 | 2025-04
2025-04-21 02:00 | flat_start_nr | 137.14 | 4 | 536 | 2025-04
2025-04-21 03:00 | flat_start_nr | 135.6 | 4 | 541 | 2025-04
2025-04-21 04:00 | flat_start_nr | 126.21 | 3 | 541 | 2025-04
2025-04-21 05:00 | flat_start_nr | 129.35 | 5 | 544 | 2025-04
2025-04-21 06:00 | flat_start_nr | 148.87 | 6 | 532 | 2025-04
2025-04-21 07:00 | flat_start_nr | 148.48 | 6 | 523 | 2025-04
2025-04-21 08:00 | flat_start_nr | 149.27 | 6 | 520 | 2025-04
2025-04-21 09:00 | flat_start_nr | 146.13 | 5 | 524 | 2025-04
2025-04-21 10:00 | flat_start_nr | 151.64 | 6 | 528 | 2025-04
2025-04-21 18:00 | flat_start_nr | 151.36 | 6 | 544 | 2025-04
2025-04-21 19:00 | flat_start_nr | 143.5 | 4 | 548 | 2025-04
2025-04-21 20:00 | flat_start_nr | 133.84 | 4 | 550 | 2025-04
2025-04-21 21:00 | flat_start_nr | 134.4 | 4 | 539 | 2025-04
2025-04-21 22:00 | flat_start_nr | 141.72 | 4 | 545 | 2025-04
2025-04-21 23:00 | flat_start_nr | 139.81 | 4 | 541 | 2025-04
2025-04-22 | flat_start_nr | 136.09 | 4 | 546 | 2025-04
2025-04-22 01:00 | flat_start_nr | 135.04 | 4 | 544 | 2025-04
2025-04-22 02:00 | flat_start_nr | 138.57 | 4 | 538 | 2025-04
2025-04-22 03:00 | flat_start_nr | 140.14 | 4 | 539 | 2025-04
2025-04-22 04:00 | flat_start_nr | 140.45 | 4 | 541 | 2025-04
2025-04-22 05:00 | flat_start_nr | 135.65 | 4 | 531 | 2025-04
2025-04-22 06:00 | flat_start_nr | 143.4 | 4 | 518 | 2025-04
2025-04-22 07:00 | flat_start_nr | 145.31 | 4 | 513 | 2025-04
2025-04-22 08:00 | flat_start_nr | 149.28 | 5 | 509 | 2025-04
2025-04-22 09:00 | flat_start_nr | 152.58 | 6 | 536 | 2025-04
2025-04-22 11:00 | flat_start_nr | 152.76 | 6 | 521 | 2025-04
2025-04-22 12:00 | flat_start_nr | 153.71 | 6 | 532 | 2025-04
2025-04-22 13:00 | flat_start_nr | 152.53 | 6 | 519 | 2025-04
2025-04-22 14:00 | flat_start_nr | 154.34 | 6 | 531 | 2025-04
2025-04-22 16:00 | flat_start_nr | 147.15 | 5 | 526 | 2025-04
2025-04-22 17:00 | flat_start_nr | 143.69 | 4 | 531 | 2025-04
2025-04-22 18:00 | flat_start_nr | 148.63 | 6 | 514 | 2025-04
2025-04-22 19:00 | flat_start_nr | 141.55 | 4 | 526 | 2025-04
2025-04-22 20:00 | flat_start_nr | 124.09 | 4 | 537 | 2025-04
2025-04-22 21:00 | flat_start_nr | 130.07 | 4 | 544 | 2025-04
2025-04-22 22:00 | flat_start_nr | 146.23 | 5 | 545 | 2025-04
2025-04-22 23:00 | flat_start_nr | 154.89 | 6 | 560 | 2025-04
2025-04-23 | flat_start_nr | 155.43 | 6 | 562 | 2025-04
2025-04-23 01:00 | flat_start_nr | 152.79 | 6 | 537 | 2025-04
2025-04-23 02:00 | flat_start_nr | 146.9 | 5 | 543 | 2025-04
2025-04-23 03:00 | flat_start_nr | 141.77 | 4 | 551 | 2025-04
2025-04-23 04:00 | flat_start_nr | 140.55 | 4 | 546 | 2025-04
2025-04-23 05:00 | flat_start_nr | 145.54 | 4 | 533 | 2025-04
2025-04-23 06:00 | flat_start_nr | 138.43 | 4 | 538 | 2025-04
2025-04-23 07:00 | flat_start_nr | 154.37 | 6 | 546 | 2025-04
2025-04-23 09:00 | flat_start_nr | 152.74 | 6 | 533 | 2025-04
2025-04-23 10:00 | flat_start_nr | 155.24 | 6 | 552 | 2025-04
2025-04-23 11:00 | flat_start_nr | 153.77 | 6 | 542 | 2025-04
2025-04-23 12:00 | flat_start_nr | 152.76 | 6 | 533 | 2025-04
2025-04-23 14:00 | flat_start_nr | 150.81 | 6 | 523 | 2025-04
2025-04-23 15:00 | flat_start_nr | 138.84 | 4 | 539 | 2025-04
2025-04-23 16:00 | flat_start_nr | 134.95 | 4 | 528 | 2025-04
2025-04-23 17:00 | flat_start_nr | 136.49 | 4 | 534 | 2025-04
2025-04-23 18:00 | flat_start_nr | 145.76 | 4 | 511 | 2025-04
2025-04-23 19:00 | flat_start_nr | 137.47 | 4 | 532 | 2025-04
2025-04-23 20:00 | flat_start_nr | 123.84 | 3 | 536 | 2025-04
2025-04-23 21:00 | flat_start_nr | 124.42 | 3 | 532 | 2025-04
2025-04-23 22:00 | flat_start_nr | 129.95 | 5 | 534 | 2025-04
2025-04-23 23:00 | flat_start_nr | 130.71 | 4 | 535 | 2025-04
2025-04-24 | flat_start_nr | 132.86 | 4 | 535 | 2025-04
2025-04-24 01:00 | flat_start_nr | 128.18 | 3 | 533 | 2025-04
2025-04-24 02:00 | flat_start_nr | 132.68 | 4 | 526 | 2025-04
2025-04-24 03:00 | flat_start_nr | 131.21 | 4 | 526 | 2025-04
2025-04-24 04:00 | flat_start_nr | 137.58 | 4 | 527 | 2025-04
2025-04-24 05:00 | flat_start_nr | 143.09 | 4 | 529 | 2025-04
2025-04-24 06:00 | flat_start_nr | 150.81 | 6 | 522 | 2025-04
2025-04-24 07:00 | flat_start_nr | 142.68 | 4 | 529 | 2025-04
2025-04-24 08:00 | flat_start_nr | 150.95 | 6 | 521 | 2025-04
2025-04-24 12:00 | flat_start_nr | 150.2 | 5 | 509 | 2025-04
2025-04-24 13:00 | flat_start_nr | 147.78 | 5 | 516 | 2025-04
2025-04-24 15:00 | flat_start_nr | 152.62 | 6 | 512 | 2025-04
2025-04-24 16:00 | flat_start_nr | 150.88 | 6 | 512 | 2025-04
2025-04-24 17:00 | flat_start_nr | 152.62 | 6 | 521 | 2025-04
2025-04-24 18:00 | flat_start_nr | 150.82 | 6 | 518 | 2025-04
2025-04-24 19:00 | flat_start_nr | 149.37 | 6 | 506 | 2025-04
2025-04-24 20:00 | flat_start_nr | 139.71 | 4 | 528 | 2025-04
2025-04-24 21:00 | flat_start_nr | 158.22 | 5 | 529 | 2025-04
2025-04-24 22:00 | normal_nr | 161.13 | 5 | 537 | 2025-04
2025-04-25 | flat_start_nr | 157.06 | 7 | 537 | 2025-04
2025-04-25 02:00 | normal_nr | 161.87 | 6 | 540 | 2025-04
2025-04-25 03:00 | flat_start_nr | 152.29 | 6 | 522 | 2025-04
2025-04-25 04:00 | flat_start_nr | 142.56 | 5 | 537 | 2025-04
2025-04-25 05:00 | flat_start_nr | 151.81 | 8 | 514 | 2025-04
2025-04-25 06:00 | flat_start_nr | 151.95 | 7 | 520 | 2025-04
2025-04-25 07:00 | flat_start_nr | 148.02 | 6 | 518 | 2025-04
2025-04-25 08:00 | flat_start_nr | 157.63 | 7 | 544 | 2025-04
2025-04-25 18:00 | flat_start_nr | 155.05 | 6 | 547 | 2025-04
2025-04-25 19:00 | flat_start_nr | 141.25 | 5 | 530 | 2025-04
2025-04-25 20:00 | flat_start_nr | 135.3 | 5 | 537 | 2025-04
2025-04-25 21:00 | flat_start_nr | 140.1 | 5 | 534 | 2025-04
2025-04-26 02:00 | normal_nr | 161.35 | 7 | 545 | 2025-04
2025-04-26 03:00 | flat_start_nr | 152.84 | 7 | 525 | 2025-04
2025-04-26 04:00 | flat_start_nr | 156.3 | 7 | 521 | 2025-04
2025-04-27 01:00 | flat_start_nr | 155.81 | 6 | 549 | 2025-04
2025-04-27 20:00 | flat_start_nr | 145.91 | 5 | 529 | 2025-04
2025-04-27 21:00 | flat_start_nr | 150.45 | 5 | 524 | 2025-04
2025-04-27 22:00 | flat_start_nr | 152.17 | 6 | 512 | 2025-04
2025-04-28 02:00 | flat_start_nr | 152.79 | 6 | 518 | 2025-04
2025-04-28 03:00 | flat_start_nr | 156.33 | 6 | 523 | 2025-04
2025-04-30 04:00 | flat_start_nr | 156.31 | 7 | 498 | 2025-04
2025-05-05 23:00 | flat_start_nr | 153.34 | 6 | 495 | 2025-05
2025-05-07 23:00 | normal_nr | 161.78 | 6 | 526 | 2025-05
2025-05-08 22:00 | flat_start_nr | 151.2 | 6 | 502 | 2025-05
2025-05-08 23:00 | flat_start_nr | 150.82 | 6 | 500 | 2025-05
2025-05-09 | flat_start_nr | 153.08 | 7 | 490 | 2025-05
2025-05-09 01:00 | flat_start_nr | 158.39 | 6 | 501 | 2025-05
2025-05-09 20:00 | flat_start_nr | 149.18 | 5 | 505 | 2025-05
2025-05-16 20:00 | flat_start_nr | 147.31 | 5 | 533 | 2025-05
2025-05-16 21:00 | flat_start_nr | 144.74 | 4 | 533 | 2025-05
2025-05-19 04:00 | flat_start_nr | 155.19 | 6 | 541 | 2025-05
2025-05-22 03:00 | flat_start_nr | 154.1 | 6 | 516 | 2025-05
2025-05-23 04:00 | flat_start_nr | 153.4 | 6 | 517 | 2025-05
2025-05-23 21:00 | flat_start_nr | 154.43 | 6 | 530 | 2025-05
2025-05-28 01:00 | flat_start_nr | 150.51 | 5 | 525 | 2025-05
2025-05-28 02:00 | flat_start_nr | 150.75 | 5 | 524 | 2025-05
2025-05-28 03:00 | flat_start_nr | 151.78 | 6 | 523 | 2025-05
2025-05-28 09:00 | flat_start_nr | 153.13 | 6 | 518 | 2025-05
2025-05-28 10:00 | flat_start_nr | 153.52 | 6 | 501 | 2025-05
2025-05-28 11:00 | flat_start_nr | 150.87 | 5 | 499 | 2025-05
2025-05-28 19:00 | flat_start_nr | 148.38 | 5 | 501 | 2025-05
2025-05-29 08:00 | flat_start_nr | 146.73 | 5 | 537 | 2025-05
2025-05-29 09:00 | flat_start_nr | 141.57 | 4 | 545 | 2025-05
2025-05-29 10:00 | flat_start_nr | 148.27 | 5 | 530 | 2025-05
2025-05-29 11:00 | flat_start_nr | 141.15 | 4 | 538 | 2025-05
2025-05-29 12:00 | flat_start_nr | 139.54 | 4 | 537 | 2025-05
2025-05-29 13:00 | flat_start_nr | 141.01 | 4 | 538 | 2025-05
2025-05-29 14:00 | flat_start_nr | 137.63 | 4 | 541 | 2025-05
2025-05-29 15:00 | flat_start_nr | 144.11 | 4 | 542 | 2025-05
2025-05-29 20:00 | flat_start_nr | 153.69 | 7 | 522 | 2025-05
2025-05-29 21:00 | flat_start_nr | 147.93 | 5 | 521 | 2025-05
2025-05-29 22:00 | flat_start_nr | 156.88 | 6 | 534 | 2025-05
2025-05-29 23:00 | flat_start_nr | 154.86 | 6 | 518 | 2025-05
2025-05-30 06:00 | flat_start_nr | 135.04 | 4 | 541 | 2025-05
2025-05-30 07:00 | flat_start_nr | 143.53 | 4 | 543 | 2025-05
2025-05-30 08:00 | flat_start_nr | 137.78 | 4 | 543 | 2025-05
2025-05-30 09:00 | flat_start_nr | 142.84 | 4 | 544 | 2025-05
2025-05-30 10:00 | flat_start_nr | 151.84 | 6 | 520 | 2025-05
2025-05-30 22:00 | normal_nr | 157.81 | 6 | 525 | 2025-05
2025-05-31 14:00 | flat_start_nr | 152.1 | 6 | 522 | 2025-05
2025-05-31 15:00 | flat_start_nr | 154.75 | 6 | 541 | 2025-05
2025-05-31 17:00 | normal_nr | 157.39 | 6 | 530 | 2025-05
2025-05-31 18:00 | flat_start_nr | 147.4 | 5 | 524 | 2025-05
2025-05-31 19:00 | flat_start_nr | 152.55 | 6 | 530 | 2025-05
2025-05-31 20:00 | flat_start_nr | 150.46 | 6 | 520 | 2025-05
2025-05-31 21:00 | flat_start_nr | 140.55 | 5 | 531 | 2025-05
2025-05-31 22:00 | flat_start_nr | 143.93 | 5 | 528 | 2025-05
2025-05-31 23:00 | flat_start_nr | 155.24 | 7 | 521 | 2025-05
2025-06-01 03:00 | flat_start_nr | 153.1 | 6 | 530 | 2025-06
2025-06-07 21:00 | normal_nr | 159.6 | 6 | 552 | 2025-06
2025-06-07 22:00 | normal_nr | 160.16 | 6 | 555 | 2025-06
2025-06-07 23:00 | flat_start_nr | 158.69 | 6 | 538 | 2025-06
2025-06-12 22:00 | normal_nr | 160.48 | 6 | 529 | 2025-06
2025-06-17 13:00 | flat_start_nr | 153.09 | 5 | 524 | 2025-06
2025-06-17 15:00 | flat_start_nr | 154.33 | 5 | 544 | 2025-06
2025-06-18 08:00 | flat_start_nr | 143.54 | 3 | 534 | 2025-06
2025-06-18 09:00 | flat_start_nr | 141.49 | 3 | 546 | 2025-06
2025-06-18 10:00 | flat_start_nr | 141.29 | 3 | 541 | 2025-06
2025-06-18 11:00 | flat_start_nr | 141.76 | 3 | 544 | 2025-06
2025-06-18 12:00 | flat_start_nr | 144.45 | 3 | 546 | 2025-06
2025-06-18 13:00 | flat_start_nr | 144.36 | 3 | 544 | 2025-06
2025-06-18 14:00 | flat_start_nr | 143.84 | 3 | 533 | 2025-06
2025-06-18 15:00 | flat_start_nr | 148.22 | 4 | 526 | 2025-06
2025-06-18 16:00 | flat_start_nr | 152.51 | 5 | 546 | 2025-06
2025-06-18 20:00 | flat_start_nr | 152.43 | 5 | 530 | 2025-06
2025-06-18 21:00 | flat_start_nr | 140.19 | 3 | 546 | 2025-06
2025-06-19 01:00 | normal_nr | 159.62 | 5 | 542 | 2025-06
2025-06-19 02:00 | flat_start_nr | 156.35 | 6 | 542 | 2025-06
2025-06-19 03:00 | flat_start_nr | 148.41 | 6 | 519 | 2025-06
2025-06-19 06:00 | flat_start_nr | 149.97 | 5 | 523 | 2025-06
2025-06-19 07:00 | flat_start_nr | 149.35 | 4 | 518 | 2025-06
2025-06-19 21:00 | normal_nr | 159.84 | 6 | 538 | 2025-06
2025-06-19 22:00 | flat_start_nr | 146.26 | 5 | 523 | 2025-06
2025-06-19 23:00 | flat_start_nr | 135.92 | 3 | 521 | 2025-06
2025-06-20 | flat_start_nr | 137.49 | 3 | 521 | 2025-06
2025-06-21 21:00 | normal_nr | 161.49 | 7 | 552 | 2025-06
2025-06-22 14:00 | flat_start_nr | 148.61 | 5 | 518 | 2025-06
2025-06-22 17:00 | flat_start_nr | 150.41 | 6 | 532 | 2025-06
2025-06-22 20:00 | flat_start_nr | 147.93 | 5 | 516 | 2025-06
2025-06-22 21:00 | flat_start_nr | 143.36 | 4 | 548 | 2025-06
2025-06-22 22:00 | flat_start_nr | 154.92 | 6 | 546 | 2025-06
2025-06-23 21:00 | flat_start_nr | 144.04 | 4 | 536 | 2025-06
2025-06-23 22:00 | flat_start_nr | 145.51 | 5 | 536 | 2025-06
2025-06-23 23:00 | flat_start_nr | 140.82 | 4 | 543 | 2025-06
2025-06-24 | flat_start_nr | 145.74 | 5 | 532 | 2025-06
2025-06-24 01:00 | flat_start_nr | 141.59 | 4 | 538 | 2025-06
2025-06-24 02:00 | flat_start_nr | 146.8 | 4 | 532 | 2025-06
2025-06-24 03:00 | flat_start_nr | 156.13 | 5 | 536 | 2025-06
2025-06-24 16:00 | flat_start_nr | 149.72 | 4 | 523 | 2025-06
2025-06-24 17:00 | flat_start_nr | 150.98 | 5 | 529 | 2025-06
2025-06-24 18:00 | flat_start_nr | 151.65 | 5 | 557 | 2025-06
2025-06-24 21:00 | flat_start_nr | 146.21 | 4 | 542 | 2025-06
2025-06-24 22:00 | flat_start_nr | 151.92 | 5 | 539 | 2025-06
2025-06-24 23:00 | flat_start_nr | 144.52 | 4 | 545 | 2025-06
2025-06-25 | flat_start_nr | 142.06 | 4 | 545 | 2025-06
2025-06-25 01:00 | flat_start_nr | 147.04 | 5 | 544 | 2025-06
2025-06-25 02:00 | flat_start_nr | 148.74 | 5 | 531 | 2025-06
2025-06-25 03:00 | flat_start_nr | 145.68 | 5 | 548 | 2025-06
2025-06-25 07:00 | flat_start_nr | 154.94 | 5 | 531 | 2025-06
2025-06-25 13:00 | flat_start_nr | 155.08 | 5 | 542 | 2025-06
2025-06-25 14:00 | flat_start_nr | 151.24 | 5 | 526 | 2025-06
2025-06-25 15:00 | flat_start_nr | 141.68 | 3 | 547 | 2025-06
2025-06-25 16:00 | flat_start_nr | 141.92 | 3 | 548 | 2025-06
2025-06-25 17:00 | flat_start_nr | 142.18 | 3 | 546 | 2025-06
2025-06-25 18:00 | flat_start_nr | 140.74 | 3 | 547 | 2025-06
2025-06-25 19:00 | flat_start_nr | 143.13 | 3 | 538 | 2025-06
2025-06-25 20:00 | flat_start_nr | 151.24 | 5 | 544 | 2025-06
2025-06-25 21:00 | flat_start_nr | 133.01 | 3 | 546 | 2025-06
2025-06-25 22:00 | flat_start_nr | 131.21 | 3 | 543 | 2025-06
2025-06-25 23:00 | flat_start_nr | 136.36 | 3 | 544 | 2025-06
2025-06-26 | flat_start_nr | 137.13 | 3 | 542 | 2025-06
2025-06-26 01:00 | flat_start_nr | 134.13 | 3 | 540 | 2025-06
2025-06-26 02:00 | flat_start_nr | 136.41 | 3 | 538 | 2025-06
2025-06-26 03:00 | flat_start_nr | 142.36 | 3 | 552 | 2025-06
2025-06-26 07:00 | flat_start_nr | 148.81 | 4 | 528 | 2025-06
2025-06-26 08:00 | flat_start_nr | 151.55 | 5 | 528 | 2025-06
2025-06-26 09:00 | flat_start_nr | 149.46 | 4 | 525 | 2025-06
2025-06-26 10:00 | flat_start_nr | 153.89 | 5 | 518 | 2025-06
2025-06-26 12:00 | flat_start_nr | 155.9 | 5 | 536 | 2025-06
2025-06-26 15:00 | flat_start_nr | 144 | 4 | 535 | 2025-06
2025-06-26 16:00 | flat_start_nr | 143.19 | 4 | 541 | 2025-06
2025-06-26 17:00 | flat_start_nr | 150.63 | 6 | 517 | 2025-06
2025-06-26 18:00 | flat_start_nr | 139.25 | 4 | 540 | 2025-06
2025-06-26 19:00 | flat_start_nr | 133.67 | 4 | 538 | 2025-06
2025-06-26 20:00 | flat_start_nr | 131.94 | 4 | 534 | 2025-06
2025-06-26 21:00 | flat_start_nr | 120.36 | 3 | 536 | 2025-06
2025-06-26 22:00 | flat_start_nr | 137.42 | 4 | 534 | 2025-06
2025-06-26 23:00 | flat_start_nr | 136.51 | 4 | 532 | 2025-06
2025-06-27 | flat_start_nr | 153.07 | 6 | 517 | 2025-06
2025-06-27 01:00 | flat_start_nr | 147.54 | 5 | 528 | 2025-06
2025-06-27 02:00 | flat_start_nr | 153.8 | 7 | 516 | 2025-06
2025-06-27 03:00 | flat_start_nr | 147.73 | 6 | 531 | 2025-06
2025-06-27 07:00 | flat_start_nr | 154.56 | 6 | 534 | 2025-06
2025-06-27 08:00 | flat_start_nr | 134.27 | 5 | 524 | 2025-06
2025-06-27 09:00 | flat_start_nr | 141.81 | 5 | 521 | 2025-06
2025-06-27 10:00 | flat_start_nr | 138.8 | 5 | 537 | 2025-06
2025-06-27 11:00 | flat_start_nr | 138.44 | 4 | 535 | 2025-06
2025-06-27 12:00 | flat_start_nr | 140.25 | 5 | 532 | 2025-06
2025-06-27 16:00 | flat_start_nr | 145.06 | 5 | 531 | 2025-06
2025-06-27 17:00 | flat_start_nr | 147.38 | 7 | 526 | 2025-06
2025-06-27 18:00 | flat_start_nr | 149.27 | 7 | 516 | 2025-06
2025-06-27 19:00 | flat_start_nr | 142.24 | 4 | 542 | 2025-06
2025-06-27 20:00 | flat_start_nr | 144.21 | 5 | 536 | 2025-06
2025-06-27 21:00 | flat_start_nr | 134.01 | 5 | 552 | 2025-06
2025-06-27 22:00 | flat_start_nr | 131.16 | 5 | 540 | 2025-06
2025-06-27 23:00 | flat_start_nr | 143.45 | 5 | 555 | 2025-06
2025-06-28 | flat_start_nr | 155.69 | 7 | 554 | 2025-06
2025-06-28 01:00 | normal_nr | 159.74 | 8 | 559 | 2025-06
2025-06-28 08:00 | flat_start_nr | 153.48 | 6 | 553 | 2025-06
2025-06-28 20:00 | flat_start_nr | 147.91 | 5 | 506 | 2025-06
2025-06-28 21:00 | flat_start_nr | 153.89 | 6 | 552 | 2025-06
2025-06-28 22:00 | flat_start_nr | 145.2 | 4 | 540 | 2025-06
2025-06-29 20:00 | flat_start_nr | 140.53 | 4 | 525 | 2025-06
2025-06-29 21:00 | flat_start_nr | 128.07 | 3 | 530 | 2025-06
2025-06-29 22:00 | flat_start_nr | 145.36 | 4 | 538 | 2025-06
2025-06-29 23:00 | flat_start_nr | 146.8 | 5 | 530 | 2025-06
2025-06-30 03:00 | flat_start_nr | 146.19 | 5 | 538 | 2025-06
2025-06-30 08:00 | flat_start_nr | 149.08 | 5 | 526 | 2025-06
2025-06-30 09:00 | flat_start_nr | 137.87 | 4 | 529 | 2025-06
2025-06-30 10:00 | flat_start_nr | 140.96 | 4 | 534 | 2025-06
2025-06-30 11:00 | flat_start_nr | 139.38 | 4 | 533 | 2025-06
2025-06-30 12:00 | flat_start_nr | 131.06 | 4 | 536 | 2025-06
2025-06-30 13:00 | flat_start_nr | 129.87 | 4 | 533 | 2025-06
2025-06-30 14:00 | flat_start_nr | 125.64 | 3 | 531 | 2025-06
2025-06-30 15:00 | flat_start_nr | 129.43 | 4 | 529 | 2025-06
2025-06-30 16:00 | flat_start_nr | 138.39 | 4 | 533 | 2025-06
2025-06-30 17:00 | flat_start_nr | 148.28 | 5 | 521 | 2025-06
2025-06-30 18:00 | flat_start_nr | 147.16 | 5 | 517 | 2025-06
2025-06-30 19:00 | flat_start_nr | 140.58 | 4 | 522 | 2025-06
2025-06-30 20:00 | flat_start_nr | 139.93 | 4 | 532 | 2025-06
2025-06-30 21:00 | flat_start_nr | 129.69 | 4 | 526 | 2025-06
2025-06-30 22:00 | flat_start_nr | 148.94 | 5 | 526 | 2025-06
2025-06-30 23:00 | flat_start_nr | 144.91 | 4 | 538 | 2025-06
2025-07-01 | flat_start_nr | 138.19 | 4 | 544 | 2025-07
2025-07-01 01:00 | flat_start_nr | 138.18 | 4 | 539 | 2025-07
2025-07-01 02:00 | flat_start_nr | 146.58 | 5 | 537 | 2025-07
2025-07-01 03:00 | flat_start_nr | 142.82 | 4 | 540 | 2025-07
2025-07-01 09:00 | flat_start_nr | 153.85 | 5 | 539 | 2025-07
2025-07-01 10:00 | flat_start_nr | 149.02 | 4 | 515 | 2025-07
2025-07-01 11:00 | flat_start_nr | 138.89 | 3 | 531 | 2025-07
2025-07-01 12:00 | flat_start_nr | 130.97 | 4 | 533 | 2025-07
2025-07-01 13:00 | flat_start_nr | 130.41 | 4 | 525 | 2025-07
2025-07-01 14:00 | flat_start_nr | 127.61 | 3 | 524 | 2025-07
2025-07-01 15:00 | flat_start_nr | 127.26 | 3 | 526 | 2025-07
2025-07-01 16:00 | flat_start_nr | 127.46 | 3 | 529 | 2025-07
2025-07-01 17:00 | flat_start_nr | 141.78 | 3 | 545 | 2025-07
2025-07-01 18:00 | flat_start_nr | 141.27 | 3 | 559 | 2025-07
2025-07-01 19:00 | flat_start_nr | 140.35 | 3 | 557 | 2025-07
2025-07-01 20:00 | flat_start_nr | 145.96 | 5 | 533 | 2025-07
2025-07-02 08:00 | flat_start_nr | 145.23 | 4 | 535 | 2025-07
2025-07-02 09:00 | flat_start_nr | 128.38 | 3 | 546 | 2025-07
2025-07-02 10:00 | flat_start_nr | 116.92 | 3 | 547 | 2025-07
2025-07-02 11:00 | flat_start_nr | 117.36 | 3 | 549 | 2025-07
2025-07-02 12:00 | flat_start_nr | 117.94 | 2 | 545 | 2025-07
2025-07-02 13:00 | flat_start_nr | 113.58 | 2 | 546 | 2025-07
2025-07-02 14:00 | flat_start_nr | 127.07 | 3 | 545 | 2025-07
2025-07-02 15:00 | flat_start_nr | 131.77 | 4 | 547 | 2025-07
2025-07-02 16:00 | flat_start_nr | 125.53 | 3 | 546 | 2025-07
2025-07-02 17:00 | flat_start_nr | 127.5 | 3 | 544 | 2025-07
2025-07-02 18:00 | flat_start_nr | 120.21 | 3 | 547 | 2025-07
2025-07-02 19:00 | flat_start_nr | 126.41 | 3 | 544 | 2025-07
2025-07-02 20:00 | flat_start_nr | 115.44 | 2 | 544 | 2025-07
2025-07-02 21:00 | flat_start_nr | 113.23 | 2 | 541 | 2025-07
2025-07-02 22:00 | flat_start_nr | 113.15 | 3 | 538 | 2025-07
2025-07-02 23:00 | flat_start_nr | 125.66 | 3 | 537 | 2025-07
2025-07-03 | flat_start_nr | 143.3 | 4 | 545 | 2025-07
2025-07-03 01:00 | flat_start_nr | 150.6 | 5 | 531 | 2025-07
2025-07-03 08:00 | flat_start_nr | 143.75 | 4 | 531 | 2025-07
2025-07-03 09:00 | flat_start_nr | 133.5 | 4 | 534 | 2025-07
2025-07-03 10:00 | flat_start_nr | 134.36 | 4 | 537 | 2025-07
2025-07-03 11:00 | flat_start_nr | 149.14 | 6 | 521 | 2025-07
2025-07-03 12:00 | flat_start_nr | 154.99 | 6 | 535 | 2025-07
2025-07-03 21:00 | flat_start_nr | 152.72 | 5 | 528 | 2025-07
2025-07-03 22:00 | flat_start_nr | 155.94 | 6 | 546 | 2025-07
2025-07-03 23:00 | normal_nr | 160.02 | 6 | 554 | 2025-07
2025-07-04 | flat_start_nr | 150.51 | 6 | 536 | 2025-07
2025-07-04 01:00 | flat_start_nr | 143.99 | 5 | 543 | 2025-07
2025-07-04 02:00 | flat_start_nr | 143.95 | 4 | 543 | 2025-07
2025-07-04 03:00 | flat_start_nr | 144.07 | 4 | 544 | 2025-07
2025-07-04 04:00 | flat_start_nr | 149.99 | 6 | 532 | 2025-07
2025-07-04 06:00 | flat_start_nr | 146.88 | 5 | 526 | 2025-07
2025-07-04 07:00 | flat_start_nr | 147.99 | 5 | 529 | 2025-07
2025-07-04 09:00 | flat_start_nr | 151.06 | 6 | 529 | 2025-07
2025-07-04 13:00 | flat_start_nr | 153.16 | 6 | 548 | 2025-07
2025-07-04 14:00 | flat_start_nr | 140.89 | 4 | 549 | 2025-07
2025-07-04 15:00 | flat_start_nr | 139.02 | 4 | 544 | 2025-07
2025-07-04 16:00 | flat_start_nr | 140.79 | 4 | 547 | 2025-07
2025-07-04 17:00 | flat_start_nr | 149.74 | 6 | 534 | 2025-07
2025-07-04 18:00 | flat_start_nr | 147.04 | 5 | 529 | 2025-07
2025-07-04 19:00 | flat_start_nr | 150.36 | 6 | 527 | 2025-07
2025-07-04 20:00 | flat_start_nr | 145.39 | 6 | 535 | 2025-07
2025-07-04 21:00 | flat_start_nr | 137.59 | 5 | 532 | 2025-07
2025-07-04 22:00 | flat_start_nr | 136 | 5 | 533 | 2025-07
2025-07-04 23:00 | flat_start_nr | 146.46 | 6 | 533 | 2025-07
2025-07-05 | flat_start_nr | 149.11 | 6 | 526 | 2025-07
2025-07-05 01:00 | flat_start_nr | 153.42 | 6 | 524 | 2025-07
2025-07-05 02:00 | flat_start_nr | 154.22 | 6 | 521 | 2025-07
2025-07-05 03:00 | flat_start_nr | 143 | 4 | 540 | 2025-07
2025-07-05 04:00 | flat_start_nr | 134.35 | 4 | 534 | 2025-07
2025-07-05 05:00 | flat_start_nr | 150.63 | 6 | 521 | 2025-07
2025-07-05 06:00 | flat_start_nr | 152.6 | 6 | 542 | 2025-07
2025-07-05 16:00 | normal_nr | 155.9 | 6 | 526 | 2025-07
2025-07-05 17:00 | flat_start_nr | 155.11 | 6 | 533 | 2025-07
2025-07-05 19:00 | flat_start_nr | 150.07 | 6 | 554 | 2025-07
2025-07-05 20:00 | flat_start_nr | 130.04 | 4 | 547 | 2025-07
2025-07-05 21:00 | flat_start_nr | 128.73 | 3 | 533 | 2025-07
2025-07-05 22:00 | flat_start_nr | 135.39 | 4 | 531 | 2025-07
2025-07-05 23:00 | flat_start_nr | 144.14 | 4 | 540 | 2025-07
2025-07-06 03:00 | flat_start_nr | 155.17 | 6 | 544 | 2025-07
2025-07-06 07:00 | flat_start_nr | 143.8 | 4 | 530 | 2025-07
2025-07-06 08:00 | flat_start_nr | 124.08 | 4 | 537 | 2025-07
2025-07-06 09:00 | flat_start_nr | 136.39 | 4 | 531 | 2025-07
2025-07-06 14:00 | flat_start_nr | 155.75 | 6 | 529 | 2025-07
2025-07-06 19:00 | flat_start_nr | 150.86 | 6 | 554 | 2025-07
2025-07-06 20:00 | flat_start_nr | 125.05 | 3 | 537 | 2025-07
2025-07-06 21:00 | flat_start_nr | 110.98 | 2 | 540 | 2025-07
2025-07-06 22:00 | flat_start_nr | 129.3 | 4 | 540 | 2025-07
2025-07-06 23:00 | flat_start_nr | 132.23 | 4 | 538 | 2025-07
2025-07-07 | flat_start_nr | 130.74 | 4 | 536 | 2025-07
2025-07-07 01:00 | flat_start_nr | 133.54 | 4 | 537 | 2025-07
2025-07-07 02:00 | flat_start_nr | 134.43 | 4 | 533 | 2025-07
2025-07-07 03:00 | flat_start_nr | 126.29 | 3 | 533 | 2025-07
2025-07-07 04:00 | flat_start_nr | 135.2 | 4 | 535 | 2025-07
2025-07-07 05:00 | flat_start_nr | 139.62 | 4 | 543 | 2025-07
2025-07-07 06:00 | flat_start_nr | 141.45 | 4 | 540 | 2025-07
2025-07-07 07:00 | flat_start_nr | 136.22 | 4 | 545 | 2025-07
2025-07-07 08:00 | flat_start_nr | 138.57 | 4 | 533 | 2025-07
2025-07-07 09:00 | flat_start_nr | 139.42 | 4 | 532 | 2025-07
2025-07-07 10:00 | flat_start_nr | 137.32 | 4 | 526 | 2025-07
2025-07-07 11:00 | flat_start_nr | 139.76 | 4 | 532 | 2025-07
2025-07-07 12:00 | flat_start_nr | 135.74 | 4 | 532 | 2025-07
2025-07-07 13:00 | flat_start_nr | 129.1 | 3 | 533 | 2025-07
2025-07-07 14:00 | flat_start_nr | 127.97 | 3 | 528 | 2025-07
2025-07-07 15:00 | flat_start_nr | 140.11 | 3 | 538 | 2025-07
2025-07-07 16:00 | flat_start_nr | 142.91 | 3 | 531 | 2025-07
2025-07-07 17:00 | flat_start_nr | 146.47 | 4 | 527 | 2025-07
2025-07-07 18:00 | flat_start_nr | 139.34 | 3 | 558 | 2025-07
2025-07-07 19:00 | flat_start_nr | 140.81 | 3 | 549 | 2025-07
2025-07-07 20:00 | flat_start_nr | 140.16 | 3 | 547 | 2025-07
2025-07-07 21:00 | flat_start_nr | 148.1 | 4 | 526 | 2025-07
2025-07-07 22:00 | normal_nr | 161.12 | 6 | 549 | 2025-07
2025-07-07 23:00 | flat_start_nr | 157.44 | 6 | 547 | 2025-07
2025-07-08 | flat_start_nr | 156.73 | 6 | 546 | 2025-07
2025-07-08 08:00 | flat_start_nr | 137.01 | 3 | 540 | 2025-07
2025-07-08 09:00 | flat_start_nr | 140.89 | 3 | 543 | 2025-07
2025-07-08 10:00 | flat_start_nr | 143.63 | 3 | 542 | 2025-07
2025-07-08 11:00 | flat_start_nr | 135.42 | 3 | 548 | 2025-07
2025-07-08 12:00 | flat_start_nr | 139.16 | 3 | 549 | 2025-07
2025-07-08 13:00 | flat_start_nr | 129.2 | 2 | 547 | 2025-07
2025-07-08 14:00 | flat_start_nr | 129.45 | 3 | 547 | 2025-07
2025-07-08 15:00 | flat_start_nr | 138.68 | 3 | 543 | 2025-07
2025-07-08 16:00 | flat_start_nr | 150.75 | 4 | 523 | 2025-07
2025-07-08 19:00 | flat_start_nr | 146.66 | 4 | 519 | 2025-07
2025-07-08 21:00 | flat_start_nr | 155.27 | 6 | 522 | 2025-07
2025-07-08 22:00 | flat_start_nr | 154.15 | 6 | 517 | 2025-07
2025-07-09 14:00 | flat_start_nr | 156.56 | 6 | 525 | 2025-07
2025-07-09 15:00 | flat_start_nr | 144.75 | 3 | 540 | 2025-07
2025-07-09 16:00 | flat_start_nr | 143.41 | 3 | 549 | 2025-07
2025-07-09 17:00 | flat_start_nr | 146.43 | 4 | 530 | 2025-07
2025-07-09 21:00 | flat_start_nr | 139.86 | 4 | 536 | 2025-07
2025-07-09 22:00 | flat_start_nr | 150.93 | 4 | 528 | 2025-07
2025-07-09 23:00 | flat_start_nr | 145.18 | 3 | 544 | 2025-07
2025-07-10 | flat_start_nr | 141.26 | 3 | 548 | 2025-07
2025-07-10 01:00 | flat_start_nr | 150.52 | 4 | 530 | 2025-07
2025-07-10 02:00 | flat_start_nr | 149.58 | 4 | 531 | 2025-07
2025-07-10 04:00 | flat_start_nr | 153.44 | 5 | 523 | 2025-07
2025-07-11 03:00 | normal_nr | 159.46 | 5 | 548 | 2025-07
2025-07-11 21:00 | flat_start_nr | 155.9 | 5 | 542 | 2025-07
2025-07-12 12:00 | flat_start_nr | 146.69 | 5 | 541 | 2025-07
2025-07-12 13:00 | flat_start_nr | 143 | 4 | 553 | 2025-07
2025-07-12 14:00 | flat_start_nr | 145.26 | 4 | 547 | 2025-07
2025-07-12 15:00 | flat_start_nr | 146.46 | 5 | 546 | 2025-07
2025-07-12 16:00 | flat_start_nr | 149.99 | 5 | 542 | 2025-07
2025-07-12 21:00 | flat_start_nr | 145.94 | 5 | 546 | 2025-07
2025-07-12 23:00 | flat_start_nr | 151.75 | 6 | 536 | 2025-07
2025-07-13 | flat_start_nr | 142.82 | 4 | 548 | 2025-07
2025-07-13 01:00 | flat_start_nr | 156.11 | 6 | 540 | 2025-07
2025-07-13 12:00 | flat_start_nr | 150.22 | 5 | 541 | 2025-07
2025-07-13 13:00 | flat_start_nr | 143.82 | 4 | 550 | 2025-07
2025-07-13 14:00 | flat_start_nr | 142.76 | 4 | 554 | 2025-07
2025-07-13 15:00 | flat_start_nr | 143.28 | 4 | 545 | 2025-07
2025-07-13 21:00 | flat_start_nr | 152.24 | 6 | 519 | 2025-07
2025-07-13 22:00 | flat_start_nr | 153.22 | 7 | 514 | 2025-07
2025-07-13 23:00 | flat_start_nr | 148.22 | 5 | 527 | 2025-07
2025-07-14 | flat_start_nr | 126.7 | 4 | 523 | 2025-07
2025-07-14 01:00 | flat_start_nr | 125.98 | 6 | 531 | 2025-07
2025-07-14 02:00 | flat_start_nr | 139.54 | 4 | 533 | 2025-07
2025-07-14 07:00 | flat_start_nr | 141.51 | 4 | 535 | 2025-07
2025-07-14 08:00 | flat_start_nr | 127.66 | 4 | 533 | 2025-07
2025-07-14 09:00 | flat_start_nr | 128.72 | 4 | 532 | 2025-07
2025-07-14 10:00 | flat_start_nr | 133.33 | 5 | 536 | 2025-07
2025-07-14 11:00 | flat_start_nr | 142.63 | 4 | 534 | 2025-07
2025-07-14 12:00 | flat_start_nr | 135.65 | 5 | 536 | 2025-07
2025-07-14 13:00 | flat_start_nr | 134.64 | 5 | 534 | 2025-07
2025-07-14 14:00 | flat_start_nr | 148.3 | 5 | 521 | 2025-07
2025-07-14 19:00 | flat_start_nr | 154.56 | 6 | 548 | 2025-07
2025-07-14 20:00 | flat_start_nr | 137.28 | 4 | 534 | 2025-07
2025-07-14 21:00 | flat_start_nr | 142.57 | 4 | 537 | 2025-07
2025-07-14 22:00 | flat_start_nr | 152.68 | 6 | 518 | 2025-07
2025-07-14 23:00 | flat_start_nr | 155.71 | 6 | 543 | 2025-07
2025-07-15 10:00 | flat_start_nr | 144.79 | 4 | 529 | 2025-07
2025-07-15 11:00 | flat_start_nr | 148.07 | 5 | 533 | 2025-07
2025-07-15 12:00 | flat_start_nr | 133.35 | 5 | 530 | 2025-07
2025-07-15 13:00 | flat_start_nr | 141.89 | 4 | 539 | 2025-07
2025-07-15 14:00 | flat_start_nr | 144.41 | 4 | 529 | 2025-07
2025-07-15 15:00 | flat_start_nr | 129.58 | 4 | 535 | 2025-07
2025-07-15 16:00 | flat_start_nr | 139.87 | 4 | 533 | 2025-07
2025-07-15 17:00 | flat_start_nr | 125.98 | 4 | 536 | 2025-07
2025-07-15 18:00 | flat_start_nr | 141.06 | 4 | 556 | 2025-07
2025-07-15 19:00 | flat_start_nr | 134.1 | 5 | 545 | 2025-07
2025-07-15 20:00 | flat_start_nr | 126.81 | 4 | 537 | 2025-07
2025-07-15 21:00 | flat_start_nr | 116.51 | 4 | 543 | 2025-07
2025-07-15 22:00 | flat_start_nr | 134.47 | 4 | 535 | 2025-07
2025-07-16 | flat_start_nr | 144.62 | 4 | 538 | 2025-07
2025-07-16 01:00 | flat_start_nr | 148.57 | 5 | 528 | 2025-07
2025-07-16 02:00 | flat_start_nr | 147.23 | 5 | 528 | 2025-07
2025-07-16 03:00 | flat_start_nr | 146.14 | 5 | 530 | 2025-07
2025-07-16 04:00 | flat_start_nr | 143.7 | 4 | 543 | 2025-07
2025-07-16 17:00 | flat_start_nr | 153.75 | 6 | 545 | 2025-07
2025-07-16 18:00 | flat_start_nr | 144.16 | 4 | 529 | 2025-07
2025-07-16 19:00 | flat_start_nr | 135.71 | 4 | 539 | 2025-07
2025-07-16 20:00 | flat_start_nr | 150.17 | 6 | 518 | 2025-07
2025-07-16 21:00 | flat_start_nr | 143.58 | 5 | 534 | 2025-07
2025-07-16 22:00 | flat_start_nr | 148.55 | 6 | 532 | 2025-07
2025-07-17 01:00 | flat_start_nr | 154.99 | 7 | 525 | 2025-07
2025-07-17 02:00 | flat_start_nr | 146.71 | 6 | 532 | 2025-07
2025-07-17 03:00 | flat_start_nr | 146.17 | 5 | 535 | 2025-07
2025-07-17 04:00 | flat_start_nr | 145.12 | 4 | 535 | 2025-07
2025-07-17 05:00 | flat_start_nr | 141.86 | 4 | 529 | 2025-07
2025-07-17 06:00 | flat_start_nr | 136.87 | 5 | 536 | 2025-07
2025-07-17 07:00 | flat_start_nr | 122.34 | 4 | 541 | 2025-07
2025-07-17 08:00 | flat_start_nr | 116.88 | 4 | 542 | 2025-07
2025-07-17 09:00 | flat_start_nr | 121.19 | 4 | 538 | 2025-07
2025-07-17 10:00 | flat_start_nr | 129.77 | 4 | 543 | 2025-07
2025-07-17 11:00 | flat_start_nr | 134.58 | 4 | 542 | 2025-07
2025-07-17 12:00 | flat_start_nr | 126.6 | 3 | 550 | 2025-07
2025-07-17 13:00 | flat_start_nr | 130.22 | 4 | 543 | 2025-07
2025-07-17 14:00 | flat_start_nr | 134.98 | 4 | 543 | 2025-07
2025-07-17 15:00 | flat_start_nr | 143.62 | 3 | 552 | 2025-07
2025-07-17 16:00 | flat_start_nr | 141.31 | 4 | 547 | 2025-07
2025-07-17 17:00 | flat_start_nr | 130.1 | 4 | 542 | 2025-07
2025-07-17 18:00 | flat_start_nr | 137.88 | 4 | 549 | 2025-07
2025-07-17 19:00 | flat_start_nr | 135.82 | 4 | 541 | 2025-07
2025-07-17 20:00 | flat_start_nr | 129.95 | 5 | 547 | 2025-07
2025-07-17 21:00 | flat_start_nr | 114.01 | 3 | 545 | 2025-07
2025-07-17 22:00 | flat_start_nr | 114.21 | 3 | 544 | 2025-07
2025-07-17 23:00 | flat_start_nr | 114.37 | 3 | 539 | 2025-07
2025-07-18 | flat_start_nr | 116.75 | 3 | 536 | 2025-07
2025-07-18 01:00 | flat_start_nr | 118.71 | 3 | 536 | 2025-07
2025-07-18 02:00 | flat_start_nr | 122.88 | 3 | 531 | 2025-07
2025-07-18 03:00 | flat_start_nr | 123.51 | 3 | 531 | 2025-07
2025-07-18 04:00 | flat_start_nr | 128.26 | 3 | 538 | 2025-07
2025-07-18 05:00 | flat_start_nr | 138.42 | 4 | 529 | 2025-07
2025-07-18 06:00 | flat_start_nr | 150.72 | 6 | 524 | 2025-07
2025-07-18 08:00 | flat_start_nr | 152.79 | 6 | 540 | 2025-07
2025-07-18 10:00 | flat_start_nr | 149.02 | 5 | 516 | 2025-07
2025-07-18 11:00 | flat_start_nr | 149.42 | 5 | 517 | 2025-07
2025-07-18 13:00 | flat_start_nr | 149.37 | 4 | 531 | 2025-07
2025-07-18 14:00 | flat_start_nr | 145.09 | 3 | 543 | 2025-07
2025-07-18 15:00 | flat_start_nr | 146.21 | 4 | 540 | 2025-07
2025-07-18 16:00 | flat_start_nr | 149.57 | 4 | 531 | 2025-07
2025-07-18 17:00 | flat_start_nr | 147.92 | 5 | 524 | 2025-07
2025-07-18 18:00 | flat_start_nr | 148.41 | 5 | 521 | 2025-07
2025-07-19 02:00 | flat_start_nr | 156.2 | 7 | 529 | 2025-07
2025-07-19 03:00 | flat_start_nr | 153.64 | 6 | 528 | 2025-07
2025-07-19 04:00 | flat_start_nr | 134.51 | 4 | 554 | 2025-07
2025-07-19 05:00 | flat_start_nr | 151.7 | 6 | 526 | 2025-07
2025-07-19 08:00 | flat_start_nr | 151.29 | 6 | 540 | 2025-07
2025-07-19 09:00 | flat_start_nr | 146.17 | 5 | 540 | 2025-07
2025-07-19 17:00 | flat_start_nr | 149.09 | 5 | 524 | 2025-07
2025-07-19 18:00 | flat_start_nr | 151.63 | 6 | 528 | 2025-07
2025-07-19 20:00 | flat_start_nr | 141.43 | 4 | 540 | 2025-07
2025-07-19 21:00 | flat_start_nr | 123.18 | 4 | 545 | 2025-07
2025-07-19 22:00 | flat_start_nr | 124.12 | 4 | 543 | 2025-07
2025-07-19 23:00 | flat_start_nr | 140.57 | 4 | 547 | 2025-07
2025-07-20 | flat_start_nr | 137.05 | 4 | 548 | 2025-07
2025-07-20 01:00 | flat_start_nr | 143.21 | 4 | 543 | 2025-07
2025-07-20 02:00 | flat_start_nr | 148.94 | 5 | 527 | 2025-07
2025-07-20 03:00 | flat_start_nr | 150.15 | 5 | 529 | 2025-07
2025-07-20 08:00 | flat_start_nr | 152.46 | 6 | 553 | 2025-07
2025-07-20 15:00 | flat_start_nr | 153.09 | 6 | 530 | 2025-07
2025-07-20 16:00 | flat_start_nr | 151.68 | 6 | 539 | 2025-07
2025-07-20 17:00 | flat_start_nr | 153.92 | 6 | 545 | 2025-07
2025-07-20 18:00 | flat_start_nr | 153 | 6 | 538 | 2025-07
2025-07-20 19:00 | flat_start_nr | 152.92 | 6 | 550 | 2025-07
2025-07-20 20:00 | flat_start_nr | 149.63 | 5 | 527 | 2025-07
2025-07-20 21:00 | flat_start_nr | 149.54 | 5 | 526 | 2025-07
2025-07-20 22:00 | flat_start_nr | 144.41 | 4 | 540 | 2025-07
2025-07-20 23:00 | flat_start_nr | 139.58 | 4 | 543 | 2025-07
2025-07-21 | flat_start_nr | 137.81 | 4 | 548 | 2025-07
2025-07-21 01:00 | flat_start_nr | 133.94 | 4 | 547 | 2025-07
2025-07-21 02:00 | flat_start_nr | 137.67 | 4 | 553 | 2025-07
2025-07-21 03:00 | flat_start_nr | 142.56 | 4 | 557 | 2025-07
2025-07-21 04:00 | flat_start_nr | 140.16 | 4 | 552 | 2025-07
2025-07-21 08:00 | flat_start_nr | 149.43 | 5 | 524 | 2025-07
2025-07-21 09:00 | flat_start_nr | 147.66 | 5 | 530 | 2025-07
2025-07-21 10:00 | flat_start_nr | 146.73 | 5 | 529 | 2025-07
2025-07-21 11:00 | flat_start_nr | 145.33 | 4 | 524 | 2025-07
2025-07-21 12:00 | flat_start_nr | 149.91 | 5 | 520 | 2025-07
2025-07-21 13:00 | flat_start_nr | 144.67 | 4 | 537 | 2025-07
2025-07-21 14:00 | flat_start_nr | 150 | 5 | 540 | 2025-07
2025-07-21 18:00 | flat_start_nr | 151.05 | 6 | 543 | 2025-07
2025-07-21 19:00 | flat_start_nr | 149.36 | 6 | 521 | 2025-07
2025-07-21 20:00 | flat_start_nr | 135.12 | 4 | 554 | 2025-07
2025-07-21 21:00 | flat_start_nr | 140.1 | 4 | 545 | 2025-07
2025-07-22 18:00 | flat_start_nr | 151.52 | 6 | 537 | 2025-07
2025-07-22 19:00 | flat_start_nr | 134.08 | 4 | 540 | 2025-07
2025-07-22 20:00 | flat_start_nr | 115.62 | 3 | 537 | 2025-07
2025-07-22 21:00 | flat_start_nr | 115.53 | 3 | 539 | 2025-07
2025-07-22 22:00 | flat_start_nr | 119.5 | 4 | 540 | 2025-07
2025-07-22 23:00 | flat_start_nr | 122.08 | 3 | 542 | 2025-07
2025-07-23 | flat_start_nr | 123.93 | 3 | 536 | 2025-07
2025-07-23 01:00 | flat_start_nr | 121.47 | 3 | 531 | 2025-07
2025-07-23 02:00 | flat_start_nr | 119.66 | 3 | 531 | 2025-07
2025-07-23 03:00 | flat_start_nr | 119.28 | 3 | 532 | 2025-07
2025-07-23 04:00 | flat_start_nr | 117.81 | 2 | 538 | 2025-07
2025-07-23 05:00 | flat_start_nr | 124.87 | 5 | 528 | 2025-07
2025-07-23 06:00 | flat_start_nr | 138.98 | 4 | 526 | 2025-07
2025-07-23 16:00 | flat_start_nr | 141.56 | 4 | 512 | 2025-07
2025-07-23 17:00 | flat_start_nr | 133.82 | 4 | 520 | 2025-07
2025-07-23 18:00 | flat_start_nr | 131.93 | 4 | 527 | 2025-07
2025-07-23 19:00 | flat_start_nr | 126.02 | 3 | 529 | 2025-07
2025-07-23 20:00 | flat_start_nr | 121.3 | 4 | 537 | 2025-07
2025-07-23 21:00 | flat_start_nr | 131.06 | 4 | 523 | 2025-07
2025-07-24 19:00 | flat_start_nr | 143.93 | 4 | 539 | 2025-07
2025-07-24 20:00 | flat_start_nr | 130.79 | 4 | 543 | 2025-07
2025-07-24 21:00 | flat_start_nr | 142.41 | 4 | 550 | 2025-07
2025-07-24 22:00 | normal_nr | 160 | 7 | 552 | 2025-07
2025-07-25 21:00 | flat_start_nr | 155.86 | 7 | 540 | 2025-07
2025-07-26 13:00 | flat_start_nr | 154.73 | 6 | 536 | 2025-07
2025-07-26 20:00 | normal_nr | 162.52 | 8 | 546 | 2025-07
2025-07-27 01:00 | flat_start_nr | 152.87 | 7 | 518 | 2025-07
2025-07-27 02:00 | flat_start_nr | 147.82 | 5 | 530 | 2025-07
2025-07-27 03:00 | flat_start_nr | 140.03 | 4 | 547 | 2025-07
2025-07-27 04:00 | flat_start_nr | 131 | 5 | 529 | 2025-07
2025-07-27 18:00 | flat_start_nr | 152.12 | 6 | 536 | 2025-07
2025-07-27 19:00 | flat_start_nr | 147.28 | 5 | 518 | 2025-07
2025-07-27 20:00 | flat_start_nr | 119.79 | 4 | 538 | 2025-07
2025-07-27 21:00 | flat_start_nr | 116.23 | 3 | 542 | 2025-07
2025-07-27 22:00 | flat_start_nr | 116.43 | 3 | 532 | 2025-07
2025-07-27 23:00 | flat_start_nr | 128.46 | 4 | 529 | 2025-07
2025-07-28 | flat_start_nr | 139.4 | 4 | 542 | 2025-07
2025-07-28 01:00 | flat_start_nr | 141.84 | 4 | 538 | 2025-07
2025-07-28 02:00 | flat_start_nr | 146.28 | 5 | 526 | 2025-07
2025-07-28 03:00 | flat_start_nr | 144.59 | 4 | 534 | 2025-07
2025-07-28 04:00 | flat_start_nr | 140.83 | 4 | 542 | 2025-07
2025-07-28 06:00 | flat_start_nr | 148.7 | 6 | 516 | 2025-07
2025-07-28 07:00 | flat_start_nr | 146.13 | 6 | 509 | 2025-07
2025-07-28 08:00 | flat_start_nr | 151.15 | 6 | 540 | 2025-07
2025-07-28 09:00 | flat_start_nr | 150.86 | 6 | 513 | 2025-07
2025-07-28 10:00 | flat_start_nr | 139.53 | 5 | 531 | 2025-07
2025-07-28 11:00 | flat_start_nr | 126.94 | 4 | 529 | 2025-07
2025-07-28 12:00 | flat_start_nr | 126.19 | 4 | 533 | 2025-07
2025-07-28 13:00 | flat_start_nr | 135.56 | 5 | 524 | 2025-07
2025-07-28 14:00 | flat_start_nr | 148.02 | 5 | 512 | 2025-07
2025-07-28 15:00 | flat_start_nr | 144.29 | 4 | 522 | 2025-07
2025-07-28 16:00 | flat_start_nr | 132.3 | 4 | 532 | 2025-07
2025-07-28 17:00 | flat_start_nr | 118.65 | 3 | 543 | 2025-07
2025-07-28 18:00 | flat_start_nr | 116.85 | 2 | 545 | 2025-07
2025-07-28 19:00 | flat_start_nr | 121.84 | 3 | 534 | 2025-07
2025-07-28 20:00 | flat_start_nr | 124.02 | 4 | 533 | 2025-07
2025-07-28 21:00 | flat_start_nr | 137.86 | 4 | 533 | 2025-07
2025-07-29 08:00 | flat_start_nr | 152.04 | 6 | 522 | 2025-07
2025-07-29 09:00 | flat_start_nr | 151.31 | 6 | 518 | 2025-07
2025-07-29 10:00 | flat_start_nr | 142.63 | 4 | 525 | 2025-07
2025-07-29 11:00 | flat_start_nr | 129.28 | 4 | 520 | 2025-07
2025-07-29 12:00 | flat_start_nr | 126.07 | 3 | 528 | 2025-07
2025-07-29 13:00 | flat_start_nr | 122.07 | 3 | 538 | 2025-07
2025-07-29 14:00 | flat_start_nr | 126.66 | 3 | 540 | 2025-07
2025-07-29 15:00 | flat_start_nr | 138.63 | 4 | 544 | 2025-07
2025-07-29 16:00 | flat_start_nr | 142.68 | 4 | 534 | 2025-07
2025-07-29 17:00 | flat_start_nr | 151.01 | 6 | 547 | 2025-07
2025-07-29 20:00 | flat_start_nr | 135.87 | 4 | 559 | 2025-07
2025-07-29 21:00 | flat_start_nr | 143.7 | 4 | 546 | 2025-07
2025-07-30 11:00 | flat_start_nr | 140.05 | 4 | 542 | 2025-07
2025-07-30 12:00 | flat_start_nr | 124.74 | 3 | 549 | 2025-07
2025-07-30 13:00 | flat_start_nr | 130.03 | 4 | 555 | 2025-07
2025-07-30 14:00 | flat_start_nr | 126.07 | 3 | 545 | 2025-07
2025-07-30 15:00 | flat_start_nr | 138.84 | 4 | 558 | 2025-07
2025-07-30 16:00 | flat_start_nr | 143.05 | 4 | 563 | 2025-07
2025-07-30 17:00 | flat_start_nr | 147.59 | 5 | 553 | 2025-07
2025-07-30 18:00 | flat_start_nr | 148.44 | 5 | 544 | 2025-07
2025-07-31 07:00 | flat_start_nr | 146.44 | 5 | 533 | 2025-07
2025-07-31 08:00 | flat_start_nr | 142.21 | 4 | 543 | 2025-07
2025-07-31 09:00 | flat_start_nr | 134.13 | 4 | 541 | 2025-07
2025-07-31 10:00 | flat_start_nr | 130.94 | 4 | 543 | 2025-07
2025-07-31 11:00 | flat_start_nr | 135.22 | 4 | 540 | 2025-07
2025-07-31 12:00 | flat_start_nr | 136.94 | 4 | 542 | 2025-07
2025-07-31 13:00 | flat_start_nr | 137.2 | 4 | 547 | 2025-07
2025-07-31 14:00 | flat_start_nr | 136.16 | 4 | 552 | 2025-07
2025-07-31 15:00 | flat_start_nr | 141.19 | 4 | 560 | 2025-07
2025-07-31 22:00 | flat_start_nr | 155.81 | 6 | 553 | 2025-07
2025-07-31 23:00 | flat_start_nr | 145.43 | 5 | 536 | 2025-07
2025-08-01 | flat_start_nr | 147.22 | 5 | 532 | 2025-08
2025-08-01 01:00 | flat_start_nr | 144.18 | 4 | 540 | 2025-08
2025-08-01 02:00 | flat_start_nr | 131.63 | 4 | 534 | 2025-08
2025-08-01 03:00 | flat_start_nr | 136.56 | 4 | 532 | 2025-08
2025-08-01 04:00 | flat_start_nr | 132.37 | 5 | 533 | 2025-08
2025-08-01 05:00 | flat_start_nr | 142.11 | 5 | 539 | 2025-08
2025-08-01 08:00 | flat_start_nr | 145.33 | 4 | 514 | 2025-08
2025-08-01 09:00 | flat_start_nr | 142.11 | 4 | 536 | 2025-08
2025-08-01 10:00 | flat_start_nr | 135.4 | 4 | 528 | 2025-08
2025-08-01 11:00 | flat_start_nr | 130.9 | 4 | 534 | 2025-08
2025-08-01 12:00 | flat_start_nr | 133.27 | 4 | 531 | 2025-08
2025-08-01 13:00 | flat_start_nr | 135.35 | 4 | 530 | 2025-08
2025-08-01 14:00 | flat_start_nr | 146.55 | 5 | 514 | 2025-08
2025-08-01 20:00 | flat_start_nr | 133.69 | 4 | 537 | 2025-08
2025-08-01 21:00 | flat_start_nr | 131.08 | 5 | 529 | 2025-08
2025-08-01 22:00 | flat_start_nr | 130.37 | 5 | 531 | 2025-08
2025-08-01 23:00 | flat_start_nr | 131.93 | 5 | 538 | 2025-08
2025-08-02 | flat_start_nr | 126.03 | 4 | 545 | 2025-08
2025-08-02 01:00 | flat_start_nr | 125.93 | 4 | 545 | 2025-08
2025-08-02 02:00 | flat_start_nr | 135.57 | 4 | 538 | 2025-08
2025-08-02 03:00 | flat_start_nr | 135.3 | 5 | 539 | 2025-08
2025-08-02 04:00 | flat_start_nr | 131.15 | 5 | 538 | 2025-08
2025-08-02 05:00 | flat_start_nr | 142.44 | 4 | 531 | 2025-08
2025-08-02 06:00 | flat_start_nr | 148.42 | 5 | 527 | 2025-08
2025-08-02 08:00 | flat_start_nr | 150.43 | 6 | 516 | 2025-08
2025-08-02 09:00 | flat_start_nr | 152.27 | 6 | 533 | 2025-08
2025-08-02 10:00 | flat_start_nr | 142.53 | 4 | 532 | 2025-08
2025-08-02 11:00 | flat_start_nr | 137.45 | 4 | 549 | 2025-08
2025-08-02 12:00 | flat_start_nr | 139.53 | 4 | 536 | 2025-08
2025-08-02 13:00 | flat_start_nr | 145.04 | 4 | 514 | 2025-08
2025-08-02 20:00 | flat_start_nr | 142.7 | 4 | 536 | 2025-08
2025-08-02 21:00 | flat_start_nr | 139.54 | 4 | 530 | 2025-08
2025-08-02 22:00 | flat_start_nr | 132.13 | 5 | 540 | 2025-08
2025-08-02 23:00 | flat_start_nr | 121.48 | 4 | 541 | 2025-08
2025-08-03 | flat_start_nr | 118.08 | 4 | 539 | 2025-08
2025-08-03 01:00 | flat_start_nr | 120.74 | 4 | 536 | 2025-08
2025-08-03 02:00 | flat_start_nr | 149.22 | 5 | 526 | 2025-08
2025-08-03 20:00 | flat_start_nr | 139.5 | 4 | 536 | 2025-08
2025-08-03 21:00 | flat_start_nr | 138.61 | 4 | 533 | 2025-08
2025-08-03 22:00 | flat_start_nr | 136.39 | 5 | 530 | 2025-08
2025-08-03 23:00 | flat_start_nr | 137.18 | 5 | 529 | 2025-08
2025-08-04 | flat_start_nr | 136.69 | 4 | 532 | 2025-08
2025-08-04 01:00 | flat_start_nr | 143.69 | 4 | 533 | 2025-08
2025-08-04 04:00 | flat_start_nr | 148.51 | 5 | 524 | 2025-08
2025-08-04 12:00 | flat_start_nr | 149.11 | 5 | 524 | 2025-08
2025-08-04 13:00 | flat_start_nr | 150.04 | 5 | 516 | 2025-08
2025-08-04 14:00 | flat_start_nr | 152.7 | 6 | 542 | 2025-08
2025-08-04 20:00 | flat_start_nr | 145.4 | 5 | 532 | 2025-08
2025-08-04 21:00 | flat_start_nr | 133.38 | 4 | 532 | 2025-08
2025-08-04 22:00 | flat_start_nr | 139.57 | 4 | 527 | 2025-08
2025-08-04 23:00 | flat_start_nr | 141.25 | 4 | 529 | 2025-08
2025-08-05 | flat_start_nr | 136.41 | 4 | 525 | 2025-08
2025-08-05 01:00 | flat_start_nr | 155.18 | 6 | 540 | 2025-08
2025-08-05 02:00 | flat_start_nr | 156.85 | 6 | 527 | 2025-08
2025-08-05 03:00 | flat_start_nr | 141.85 | 4 | 532 | 2025-08
2025-08-05 04:00 | flat_start_nr | 136.59 | 5 | 528 | 2025-08
2025-08-05 05:00 | flat_start_nr | 146.6 | 6 | 512 | 2025-08
2025-08-05 06:00 | flat_start_nr | 148.72 | 7 | 528 | 2025-08
2025-08-05 07:00 | flat_start_nr | 151 | 7 | 519 | 2025-08
2025-08-05 09:00 | flat_start_nr | 150.28 | 6 | 511 | 2025-08
2025-08-05 10:00 | flat_start_nr | 143.66 | 4 | 519 | 2025-08
2025-08-05 11:00 | flat_start_nr | 141.3 | 4 | 527 | 2025-08
2025-08-05 12:00 | flat_start_nr | 142.68 | 4 | 520 | 2025-08
2025-08-05 13:00 | flat_start_nr | 144.06 | 4 | 519 | 2025-08
2025-08-05 14:00 | flat_start_nr | 146.84 | 5 | 526 | 2025-08
2025-08-05 15:00 | flat_start_nr | 144.16 | 4 | 525 | 2025-08
2025-08-05 16:00 | flat_start_nr | 148.88 | 5 | 517 | 2025-08
2025-08-05 20:00 | flat_start_nr | 154.62 | 5 | 543 | 2025-08
2025-08-05 21:00 | flat_start_nr | 142.8 | 4 | 539 | 2025-08
2025-08-05 22:00 | flat_start_nr | 140.89 | 4 | 534 | 2025-08
2025-08-05 23:00 | flat_start_nr | 139.89 | 4 | 538 | 2025-08
2025-08-06 | flat_start_nr | 149.13 | 5 | 519 | 2025-08
2025-08-06 01:00 | flat_start_nr | 151.87 | 6 | 531 | 2025-08
2025-08-06 02:00 | flat_start_nr | 154.61 | 6 | 549 | 2025-08
2025-08-06 03:00 | flat_start_nr | 151.51 | 6 | 530 | 2025-08
2025-08-06 04:00 | flat_start_nr | 139.07 | 4 | 542 | 2025-08
2025-08-06 06:00 | flat_start_nr | 149.39 | 6 | 517 | 2025-08
2025-08-06 08:00 | flat_start_nr | 154.91 | 6 | 540 | 2025-08
2025-08-06 09:00 | flat_start_nr | 143.61 | 4 | 540 | 2025-08
2025-08-06 10:00 | flat_start_nr | 137.26 | 4 | 539 | 2025-08
2025-08-06 11:00 | flat_start_nr | 136.39 | 4 | 539 | 2025-08
2025-08-06 12:00 | flat_start_nr | 128.17 | 3 | 543 | 2025-08
2025-08-06 13:00 | flat_start_nr | 129.25 | 3 | 540 | 2025-08
2025-08-06 14:00 | flat_start_nr | 130.83 | 4 | 537 | 2025-08
2025-08-06 15:00 | flat_start_nr | 139.99 | 4 | 542 | 2025-08
2025-08-06 16:00 | flat_start_nr | 149.67 | 6 | 518 | 2025-08
2025-08-06 17:00 | flat_start_nr | 153.25 | 6 | 530 | 2025-08
2025-08-06 20:00 | flat_start_nr | 155.3 | 6 | 554 | 2025-08
2025-08-07 10:00 | flat_start_nr | 153.58 | 6 | 549 | 2025-08
2025-08-07 11:00 | flat_start_nr | 150.79 | 6 | 525 | 2025-08
2025-08-07 12:00 | flat_start_nr | 140.34 | 4 | 538 | 2025-08
2025-08-07 13:00 | flat_start_nr | 139.79 | 4 | 532 | 2025-08
2025-08-07 14:00 | flat_start_nr | 144.31 | 4 | 530 | 2025-08
2025-08-07 15:00 | flat_start_nr | 145.41 | 4 | 524 | 2025-08
2025-08-07 23:00 | flat_start_nr | 155.23 | 6 | 557 | 2025-08
2025-08-08 | flat_start_nr | 153.08 | 6 | 528 | 2025-08
2025-08-08 02:00 | flat_start_nr | 151.57 | 6 | 538 | 2025-08
2025-08-08 19:00 | flat_start_nr | 146.52 | 6 | 540 | 2025-08
2025-08-08 20:00 | flat_start_nr | 123.12 | 4 | 543 | 2025-08
2025-08-08 21:00 | flat_start_nr | 135.89 | 5 | 546 | 2025-08
2025-08-08 22:00 | flat_start_nr | 148.75 | 6 | 536 | 2025-08
2025-08-08 23:00 | flat_start_nr | 157.9 | 7 | 552 | 2025-08
2025-08-09 15:00 | flat_start_nr | 152.94 | 6 | 547 | 2025-08
2025-08-09 16:00 | flat_start_nr | 151.79 | 6 | 529 | 2025-08
2025-08-09 20:00 | flat_start_nr | 141.9 | 3 | 553 | 2025-08
2025-08-09 21:00 | flat_start_nr | 132.93 | 4 | 545 | 2025-08
2025-08-09 22:00 | flat_start_nr | 129.42 | 4 | 546 | 2025-08
2025-08-09 23:00 | flat_start_nr | 132.64 | 4 | 545 | 2025-08
2025-08-10 | flat_start_nr | 133.76 | 4 | 551 | 2025-08
2025-08-10 01:00 | flat_start_nr | 127.45 | 3 | 549 | 2025-08
2025-08-10 02:00 | flat_start_nr | 152.77 | 6 | 527 | 2025-08
2025-08-10 03:00 | flat_start_nr | 129.07 | 3 | 543 | 2025-08
2025-08-10 04:00 | flat_start_nr | 120.69 | 3 | 536 | 2025-08
2025-08-10 05:00 | flat_start_nr | 136.1 | 4 | 538 | 2025-08
2025-08-10 06:00 | flat_start_nr | 142.63 | 4 | 529 | 2025-08
2025-08-10 09:00 | flat_start_nr | 155.47 | 6 | 532 | 2025-08
2025-08-10 10:00 | flat_start_nr | 151.49 | 6 | 532 | 2025-08
2025-08-10 11:00 | flat_start_nr | 149.38 | 5 | 533 | 2025-08
2025-08-10 12:00 | flat_start_nr | 148.14 | 5 | 535 | 2025-08
2025-08-10 13:00 | flat_start_nr | 152.22 | 6 | 534 | 2025-08
2025-08-10 14:00 | flat_start_nr | 150.28 | 5 | 528 | 2025-08
2025-08-10 15:00 | flat_start_nr | 146.45 | 5 | 532 | 2025-08
2025-08-10 16:00 | flat_start_nr | 133.59 | 4 | 547 | 2025-08
2025-08-10 18:00 | flat_start_nr | 138.44 | 4 | 556 | 2025-08
2025-08-10 19:00 | flat_start_nr | 135.44 | 4 | 550 | 2025-08
2025-08-10 20:00 | flat_start_nr | 128.62 | 3 | 548 | 2025-08
2025-08-10 21:00 | flat_start_nr | 152.03 | 5 | 529 | 2025-08
2025-08-11 | flat_start_nr | 155.08 | 6 | 531 | 2025-08
2025-08-11 01:00 | flat_start_nr | 141.43 | 4 | 537 | 2025-08
2025-08-11 02:00 | flat_start_nr | 140.54 | 4 | 535 | 2025-08
2025-08-11 10:00 | flat_start_nr | 156.51 | 6 | 527 | 2025-08
2025-08-11 11:00 | flat_start_nr | 154.83 | 6 | 537 | 2025-08
2025-08-11 12:00 | flat_start_nr | 154.22 | 6 | 523 | 2025-08
2025-08-11 13:00 | flat_start_nr | 150.49 | 5 | 521 | 2025-08
2025-08-11 14:00 | flat_start_nr | 140.01 | 4 | 534 | 2025-08
2025-08-11 15:00 | flat_start_nr | 151.33 | 6 | 512 | 2025-08
2025-08-11 20:00 | flat_start_nr | 149.99 | 4 | 521 | 2025-08
2025-08-11 21:00 | flat_start_nr | 141.36 | 3 | 533 | 2025-08
2025-08-11 22:00 | flat_start_nr | 124.78 | 3 | 534 | 2025-08
2025-08-11 23:00 | flat_start_nr | 124.26 | 3 | 520 | 2025-08
2025-08-12 | flat_start_nr | 123.48 | 3 | 523 | 2025-08
2025-08-12 01:00 | flat_start_nr | 122.18 | 3 | 519 | 2025-08
2025-08-12 02:00 | flat_start_nr | 123.83 | 3 | 520 | 2025-08
2025-08-12 03:00 | flat_start_nr | 132.44 | 4 | 512 | 2025-08
2025-08-12 04:00 | flat_start_nr | 128.89 | 3 | 512 | 2025-08
2025-08-12 05:00 | flat_start_nr | 138.86 | 4 | 513 | 2025-08
2025-08-12 10:00 | flat_start_nr | 154.8 | 6 | 524 | 2025-08
2025-08-12 11:00 | flat_start_nr | 145.45 | 5 | 511 | 2025-08
2025-08-12 12:00 | flat_start_nr | 136.27 | 4 | 521 | 2025-08
2025-08-12 13:00 | flat_start_nr | 132.95 | 4 | 519 | 2025-08
2025-08-12 14:00 | flat_start_nr | 131.03 | 4 | 515 | 2025-08
2025-08-12 15:00 | flat_start_nr | 138.08 | 4 | 517 | 2025-08
2025-08-12 20:00 | flat_start_nr | 151.29 | 5 | 496 | 2025-08
2025-08-12 21:00 | flat_start_nr | 128.03 | 3 | 512 | 2025-08
2025-08-12 22:00 | flat_start_nr | 135.34 | 5 | 509 | 2025-08
2025-08-12 23:00 | flat_start_nr | 135.55 | 5 | 508 | 2025-08
2025-08-13 | flat_start_nr | 136.31 | 4 | 508 | 2025-08
2025-08-13 01:00 | flat_start_nr | 135.23 | 5 | 517 | 2025-08
2025-08-13 02:00 | flat_start_nr | 142.67 | 5 | 512 | 2025-08
2025-08-13 03:00 | flat_start_nr | 147.51 | 6 | 506 | 2025-08
2025-08-13 04:00 | flat_start_nr | 153.53 | 7 | 498 | 2025-08
2025-08-13 08:00 | flat_start_nr | 153.61 | 6 | 529 | 2025-08
2025-08-13 09:00 | flat_start_nr | 149.87 | 5 | 505 | 2025-08
2025-08-13 21:00 | flat_start_nr | 155.13 | 7 | 535 | 2025-08
2025-08-13 22:00 | flat_start_nr | 148.49 | 6 | 543 | 2025-08
2025-08-13 23:00 | flat_start_nr | 142.36 | 5 | 549 | 2025-08
2025-08-14 | flat_start_nr | 140.52 | 5 | 549 | 2025-08
2025-08-14 01:00 | flat_start_nr | 147 | 6 | 545 | 2025-08
2025-08-14 02:00 | flat_start_nr | 158.21 | 6 | 555 | 2025-08
2025-08-14 04:00 | flat_start_nr | 149.6 | 5 | 539 | 2025-08
2025-08-14 20:00 | flat_start_nr | 138.28 | 3 | 552 | 2025-08
2025-08-14 21:00 | flat_start_nr | 125.84 | 3 | 542 | 2025-08
2025-08-14 22:00 | flat_start_nr | 125.63 | 3 | 540 | 2025-08
2025-08-14 23:00 | flat_start_nr | 130.17 | 4 | 547 | 2025-08
2025-08-15 | flat_start_nr | 132.2 | 4 | 546 | 2025-08
2025-08-15 01:00 | flat_start_nr | 147.47 | 5 | 533 | 2025-08
2025-08-15 02:00 | flat_start_nr | 147.33 | 5 | 536 | 2025-08
2025-08-15 20:00 | flat_start_nr | 138.41 | 4 | 540 | 2025-08
2025-08-15 21:00 | flat_start_nr | 146.57 | 5 | 536 | 2025-08
2025-08-16 20:00 | flat_start_nr | 158.34 | 7 | 540 | 2025-08
2025-08-17 13:00 | flat_start_nr | 152.42 | 6 | 526 | 2025-08
2025-08-17 20:00 | flat_start_nr | 135.59 | 4 | 530 | 2025-08
2025-08-17 21:00 | flat_start_nr | 134.98 | 4 | 529 | 2025-08
2025-08-17 22:00 | flat_start_nr | 133.62 | 4 | 534 | 2025-08
2025-08-17 23:00 | flat_start_nr | 154.24 | 6 | 514 | 2025-08
2025-08-18 | flat_start_nr | 147.27 | 5 | 534 | 2025-08
2025-08-18 01:00 | flat_start_nr | 155.35 | 6 | 550 | 2025-08
2025-08-18 02:00 | flat_start_nr | 154.66 | 6 | 525 | 2025-08
2025-08-18 03:00 | flat_start_nr | 138.93 | 4 | 539 | 2025-08
2025-08-18 04:00 | flat_start_nr | 129.63 | 4 | 537 | 2025-08
2025-08-18 05:00 | flat_start_nr | 142.7 | 4 | 519 | 2025-08
2025-08-18 06:00 | flat_start_nr | 142.54 | 4 | 525 | 2025-08
2025-08-18 07:00 | flat_start_nr | 140.44 | 4 | 539 | 2025-08
2025-08-18 08:00 | flat_start_nr | 137.06 | 4 | 529 | 2025-08
2025-08-18 09:00 | flat_start_nr | 150.07 | 5 | 514 | 2025-08
2025-08-18 11:00 | flat_start_nr | 150.58 | 6 | 518 | 2025-08
2025-08-18 12:00 | flat_start_nr | 140.99 | 4 | 545 | 2025-08
2025-08-18 13:00 | flat_start_nr | 149.67 | 5 | 532 | 2025-08
2025-08-18 14:00 | flat_start_nr | 153.64 | 6 | 524 | 2025-08
2025-08-18 15:00 | flat_start_nr | 149.2 | 5 | 524 | 2025-08
2025-08-18 20:00 | flat_start_nr | 149.54 | 4 | 527 | 2025-08
2025-08-18 21:00 | flat_start_nr | 136.1 | 4 | 533 | 2025-08
2025-08-18 22:00 | flat_start_nr | 142.6 | 4 | 530 | 2025-08
2025-08-18 23:00 | flat_start_nr | 138.95 | 4 | 540 | 2025-08
2025-08-19 | flat_start_nr | 136.29 | 4 | 532 | 2025-08
2025-08-19 01:00 | flat_start_nr | 146.79 | 5 | 524 | 2025-08
2025-08-19 02:00 | flat_start_nr | 133.83 | 4 | 526 | 2025-08
2025-08-19 03:00 | flat_start_nr | 124.02 | 3 | 530 | 2025-08
2025-08-19 04:00 | flat_start_nr | 125.96 | 3 | 529 | 2025-08
2025-08-19 05:00 | flat_start_nr | 134.59 | 4 | 517 | 2025-08
2025-08-19 06:00 | flat_start_nr | 136.2 | 4 | 525 | 2025-08
2025-08-19 07:00 | flat_start_nr | 136.88 | 4 | 526 | 2025-08
2025-08-19 08:00 | flat_start_nr | 143.17 | 4 | 517 | 2025-08
2025-08-19 09:00 | flat_start_nr | 136.14 | 4 | 517 | 2025-08
2025-08-19 10:00 | flat_start_nr | 134.81 | 4 | 514 | 2025-08
2025-08-19 11:00 | flat_start_nr | 142.22 | 4 | 509 | 2025-08
2025-08-19 12:00 | flat_start_nr | 134.53 | 4 | 506 | 2025-08
2025-08-19 13:00 | flat_start_nr | 133.81 | 4 | 513 | 2025-08
2025-08-19 14:00 | flat_start_nr | 140.59 | 4 | 507 | 2025-08
2025-08-19 15:00 | flat_start_nr | 142.05 | 4 | 514 | 2025-08
2025-08-19 20:00 | flat_start_nr | 145.85 | 4 | 529 | 2025-08
2025-08-19 21:00 | flat_start_nr | 144.54 | 3 | 536 | 2025-08
2025-08-19 22:00 | flat_start_nr | 135.61 | 4 | 537 | 2025-08
2025-08-19 23:00 | flat_start_nr | 134.14 | 4 | 522 | 2025-08
2025-08-20 | flat_start_nr | 120.93 | 3 | 529 | 2025-08
2025-08-20 01:00 | flat_start_nr | 137.36 | 5 | 531 | 2025-08
2025-08-20 02:00 | flat_start_nr | 151.36 | 5 | 531 | 2025-08
2025-08-20 04:00 | flat_start_nr | 156.04 | 6 | 541 | 2025-08
2025-08-20 12:00 | flat_start_nr | 155.4 | 6 | 541 | 2025-08
2025-08-20 13:00 | flat_start_nr | 153.32 | 6 | 528 | 2025-08
2025-08-20 14:00 | flat_start_nr | 142.41 | 4 | 541 | 2025-08
2025-08-20 20:00 | flat_start_nr | 132.02 | 4 | 538 | 2025-08
2025-08-20 21:00 | flat_start_nr | 144.24 | 4 | 532 | 2025-08
2025-08-20 22:00 | flat_start_nr | 154.4 | 6 | 523 | 2025-08
2025-08-21 03:00 | flat_start_nr | 153.28 | 6 | 523 | 2025-08
2025-08-21 04:00 | flat_start_nr | 135.03 | 4 | 542 | 2025-08
2025-08-21 05:00 | flat_start_nr | 140.97 | 4 | 541 | 2025-08
2025-08-21 07:00 | flat_start_nr | 153.28 | 6 | 528 | 2025-08
2025-08-21 08:00 | flat_start_nr | 147.71 | 5 | 527 | 2025-08
2025-08-21 09:00 | flat_start_nr | 148.43 | 5 | 525 | 2025-08
2025-08-21 10:00 | flat_start_nr | 149.27 | 5 | 530 | 2025-08
2025-08-21 11:00 | flat_start_nr | 150.44 | 5 | 531 | 2025-08
2025-08-21 12:00 | flat_start_nr | 154.86 | 7 | 551 | 2025-08
2025-08-21 20:00 | flat_start_nr | 143.7 | 4 | 541 | 2025-08
2025-08-22 09:00 | flat_start_nr | 151.97 | 6 | 518 | 2025-08
2025-08-22 10:00 | flat_start_nr | 138.09 | 4 | 524 | 2025-08
2025-08-22 11:00 | flat_start_nr | 148.69 | 5 | 513 | 2025-08
2025-08-22 12:00 | flat_start_nr | 139.61 | 4 | 529 | 2025-08
2025-08-22 13:00 | flat_start_nr | 131.5 | 4 | 521 | 2025-08
2025-08-22 14:00 | flat_start_nr | 138.59 | 4 | 523 | 2025-08
2025-08-22 20:00 | flat_start_nr | 141.1 | 3 | 538 | 2025-08
2025-08-22 21:00 | flat_start_nr | 133.31 | 4 | 526 | 2025-08
2025-08-22 22:00 | flat_start_nr | 129.36 | 4 | 523 | 2025-08
2025-08-22 23:00 | flat_start_nr | 136.53 | 4 | 520 | 2025-08
2025-08-23 | flat_start_nr | 138.28 | 4 | 529 | 2025-08
2025-08-23 01:00 | flat_start_nr | 140.73 | 4 | 530 | 2025-08
2025-08-23 02:00 | flat_start_nr | 139.11 | 4 | 531 | 2025-08
2025-08-23 03:00 | flat_start_nr | 138.76 | 4 | 530 | 2025-08
2025-08-23 04:00 | flat_start_nr | 138.69 | 4 | 527 | 2025-08
2025-08-23 05:00 | flat_start_nr | 147.45 | 5 | 497 | 2025-08
2025-08-23 06:00 | flat_start_nr | 151.05 | 6 | 525 | 2025-08
2025-08-23 11:00 | flat_start_nr | 154.54 | 6 | 519 | 2025-08
2025-08-23 12:00 | flat_start_nr | 153.87 | 6 | 520 | 2025-08
2025-08-23 13:00 | flat_start_nr | 149.59 | 5 | 505 | 2025-08
2025-08-23 14:00 | flat_start_nr | 146.88 | 5 | 504 | 2025-08
2025-08-23 15:00 | flat_start_nr | 143.96 | 4 | 520 | 2025-08
2025-08-23 16:00 | flat_start_nr | 152.67 | 6 | 521 | 2025-08
2025-08-23 17:00 | flat_start_nr | 152.25 | 6 | 519 | 2025-08
2025-08-23 18:00 | flat_start_nr | 137.86 | 4 | 535 | 2025-08
2025-08-23 19:00 | flat_start_nr | 143.63 | 4 | 520 | 2025-08
2025-08-23 20:00 | flat_start_nr | 149.88 | 5 | 525 | 2025-08
2025-08-23 21:00 | flat_start_nr | 157 | 5 | 535 | 2025-08
2025-08-23 22:00 | flat_start_nr | 152.96 | 5 | 528 | 2025-08
2025-08-24 13:00 | flat_start_nr | 151.7 | 6 | 513 | 2025-08
2025-08-24 14:00 | flat_start_nr | 142.18 | 4 | 531 | 2025-08
2025-08-24 15:00 | flat_start_nr | 151.5 | 6 | 509 | 2025-08
2025-08-24 16:00 | flat_start_nr | 151.24 | 6 | 511 | 2025-08
2025-08-24 20:00 | flat_start_nr | 146.58 | 4 | 535 | 2025-08
2025-08-25 01:00 | normal_nr | 160.86 | 7 | 542 | 2025-08
2025-08-25 02:00 | flat_start_nr | 151.06 | 6 | 518 | 2025-08
2025-08-25 03:00 | flat_start_nr | 145.57 | 6 | 524 | 2025-08
2025-08-25 04:00 | flat_start_nr | 141.04 | 5 | 524 | 2025-08
2025-08-25 05:00 | flat_start_nr | 143.21 | 5 | 519 | 2025-08
2025-08-25 06:00 | flat_start_nr | 144.75 | 4 | 522 | 2025-08
2025-08-25 09:00 | flat_start_nr | 132 | 4 | 534 | 2025-08
2025-08-25 10:00 | flat_start_nr | 129.23 | 3 | 525 | 2025-08
2025-08-25 11:00 | flat_start_nr | 131.93 | 4 | 523 | 2025-08
2025-08-25 12:00 | flat_start_nr | 133.54 | 4 | 527 | 2025-08
2025-08-25 13:00 | flat_start_nr | 132.17 | 4 | 526 | 2025-08
2025-08-25 14:00 | flat_start_nr | 128.54 | 3 | 528 | 2025-08
2025-08-25 15:00 | flat_start_nr | 151.26 | 5 | 506 | 2025-08
2025-08-25 16:00 | flat_start_nr | 153.04 | 5 | 523 | 2025-08
2025-08-25 18:00 | flat_start_nr | 146.06 | 5 | 508 | 2025-08
2025-08-25 19:00 | flat_start_nr | 143.69 | 4 | 528 | 2025-08
2025-08-25 20:00 | flat_start_nr | 141.39 | 3 | 534 | 2025-08
2025-08-25 21:00 | flat_start_nr | 146.03 | 4 | 530 | 2025-08
2025-08-25 22:00 | flat_start_nr | 139.75 | 5 | 523 | 2025-08
2025-08-25 23:00 | flat_start_nr | 143.04 | 5 | 526 | 2025-08
2025-08-26 | flat_start_nr | 144.73 | 5 | 530 | 2025-08
2025-08-26 01:00 | flat_start_nr | 141.11 | 5 | 526 | 2025-08
2025-08-26 02:00 | flat_start_nr | 154.27 | 7 | 508 | 2025-08
2025-08-26 03:00 | flat_start_nr | 146.04 | 6 | 525 | 2025-08
2025-08-26 04:00 | flat_start_nr | 133.1 | 5 | 523 | 2025-08
2025-08-26 05:00 | flat_start_nr | 141.4 | 5 | 520 | 2025-08
2025-08-26 09:00 | flat_start_nr | 146.65 | 5 | 507 | 2025-08
2025-08-26 10:00 | flat_start_nr | 134.91 | 4 | 522 | 2025-08
2025-08-26 11:00 | flat_start_nr | 131.7 | 4 | 521 | 2025-08
2025-08-26 12:00 | flat_start_nr | 129.6 | 4 | 526 | 2025-08
2025-08-26 13:00 | flat_start_nr | 128.88 | 3 | 528 | 2025-08
2025-08-26 14:00 | flat_start_nr | 129.51 | 4 | 525 | 2025-08
2025-08-26 15:00 | flat_start_nr | 152.58 | 6 | 528 | 2025-08
2025-08-26 18:00 | flat_start_nr | 142.91 | 4 | 516 | 2025-08
2025-08-26 19:00 | flat_start_nr | 147.11 | 5 | 520 | 2025-08
2025-08-26 20:00 | flat_start_nr | 141.73 | 3 | 528 | 2025-08
2025-08-26 21:00 | flat_start_nr | 155.28 | 6 | 529 | 2025-08
2025-08-27 03:00 | flat_start_nr | 155.33 | 6 | 530 | 2025-08
2025-08-27 04:00 | flat_start_nr | 139.26 | 4 | 523 | 2025-08
2025-08-27 05:00 | flat_start_nr | 144.8 | 4 | 508 | 2025-08
2025-08-27 06:00 | flat_start_nr | 139.65 | 4 | 529 | 2025-08
2025-08-27 07:00 | flat_start_nr | 151.09 | 6 | 525 | 2025-08
2025-08-27 10:00 | flat_start_nr | 133.34 | 4 | 521 | 2025-08
2025-08-27 11:00 | flat_start_nr | 129.59 | 4 | 524 | 2025-08
2025-08-27 12:00 | flat_start_nr | 129.05 | 3 | 527 | 2025-08
2025-08-27 13:00 | flat_start_nr | 138.57 | 4 | 520 | 2025-08
2025-08-27 14:00 | flat_start_nr | 140.25 | 4 | 524 | 2025-08
2025-08-27 19:00 | flat_start_nr | 142.83 | 4 | 531 | 2025-08
2025-08-27 20:00 | flat_start_nr | 129.21 | 3 | 532 | 2025-08
2025-08-27 21:00 | flat_start_nr | 150.64 | 5 | 525 | 2025-08
2025-08-27 22:00 | flat_start_nr | 156.76 | 6 | 537 | 2025-08
2025-08-27 23:00 | flat_start_nr | 157.7 | 6 | 529 | 2025-08
2025-08-28 | flat_start_nr | 157.67 | 6 | 528 | 2025-08
2025-08-28 01:00 | flat_start_nr | 150.67 | 6 | 521 | 2025-08
2025-08-28 02:00 | flat_start_nr | 151.27 | 5 | 523 | 2025-08
2025-08-28 03:00 | flat_start_nr | 153.27 | 6 | 512 | 2025-08
2025-08-28 04:00 | flat_start_nr | 142.36 | 4 | 542 | 2025-08
2025-08-28 05:00 | flat_start_nr | 142.46 | 4 | 542 | 2025-08
2025-08-28 09:00 | flat_start_nr | 151.27 | 6 | 514 | 2025-08
2025-08-28 10:00 | flat_start_nr | 140.66 | 4 | 536 | 2025-08
2025-08-28 11:00 | flat_start_nr | 142.85 | 4 | 531 | 2025-08
2025-08-28 12:00 | flat_start_nr | 147.22 | 5 | 518 | 2025-08
2025-08-28 13:00 | flat_start_nr | 150.87 | 6 | 508 | 2025-08
2025-08-28 19:00 | flat_start_nr | 153.79 | 6 | 537 | 2025-08
2025-08-28 20:00 | flat_start_nr | 135 | 4 | 524 | 2025-08
2025-08-28 21:00 | flat_start_nr | 139.54 | 4 | 525 | 2025-08
2025-08-28 22:00 | flat_start_nr | 143.43 | 4 | 520 | 2025-08
2025-08-28 23:00 | flat_start_nr | 138.23 | 4 | 530 | 2025-08
2025-08-29 | flat_start_nr | 126.8 | 3 | 529 | 2025-08
2025-08-29 01:00 | flat_start_nr | 125.53 | 3 | 532 | 2025-08
2025-08-29 02:00 | flat_start_nr | 129.74 | 4 | 535 | 2025-08
2025-08-29 03:00 | flat_start_nr | 138.2 | 4 | 529 | 2025-08
2025-08-29 04:00 | flat_start_nr | 142.22 | 4 | 525 | 2025-08
2025-08-29 05:00 | flat_start_nr | 145.29 | 4 | 516 | 2025-08
2025-08-29 10:00 | flat_start_nr | 141.85 | 4 | 506 | 2025-08
2025-08-29 11:00 | flat_start_nr | 128.58 | 3 | 515 | 2025-08
2025-08-29 12:00 | flat_start_nr | 127.85 | 3 | 519 | 2025-08
2025-08-29 13:00 | flat_start_nr | 128.42 | 3 | 521 | 2025-08
2025-08-29 14:00 | flat_start_nr | 132.52 | 4 | 520 | 2025-08
2025-08-29 15:00 | flat_start_nr | 135.82 | 4 | 529 | 2025-08
2025-08-29 16:00 | flat_start_nr | 145.21 | 3 | 537 | 2025-08
2025-08-29 18:00 | flat_start_nr | 150.25 | 6 | 518 | 2025-08
2025-08-29 19:00 | flat_start_nr | 148.73 | 4 | 542 | 2025-08
2025-08-29 20:00 | flat_start_nr | 129.69 | 4 | 540 | 2025-08
2025-08-29 21:00 | flat_start_nr | 129.12 | 3 | 542 | 2025-08
2025-08-29 22:00 | flat_start_nr | 128.32 | 3 | 545 | 2025-08
2025-08-29 23:00 | flat_start_nr | 123.12 | 3 | 537 | 2025-08
2025-08-30 | flat_start_nr | 117.86 | 3 | 545 | 2025-08
2025-08-30 01:00 | flat_start_nr | 117.61 | 2 | 543 | 2025-08
2025-08-30 02:00 | flat_start_nr | 117.71 | 3 | 543 | 2025-08
2025-08-30 03:00 | flat_start_nr | 117.43 | 2 | 543 | 2025-08
2025-08-30 04:00 | flat_start_nr | 123.92 | 3 | 537 | 2025-08
2025-08-30 05:00 | flat_start_nr | 130.61 | 4 | 548 | 2025-08
2025-08-30 09:00 | flat_start_nr | 149.13 | 5 | 517 | 2025-08
2025-08-30 10:00 | flat_start_nr | 136.1 | 4 | 530 | 2025-08
2025-08-30 11:00 | flat_start_nr | 127.24 | 3 | 537 | 2025-08
2025-08-30 12:00 | flat_start_nr | 124.16 | 3 | 538 | 2025-08
2025-08-30 13:00 | flat_start_nr | 132.34 | 4 | 532 | 2025-08
2025-08-30 14:00 | flat_start_nr | 137.64 | 4 | 540 | 2025-08
2025-08-30 15:00 | flat_start_nr | 140.17 | 4 | 541 | 2025-08
2025-08-30 16:00 | flat_start_nr | 131.14 | 4 | 540 | 2025-08
2025-08-30 17:00 | flat_start_nr | 132.25 | 4 | 540 | 2025-08
2025-08-30 18:00 | flat_start_nr | 133.53 | 4 | 541 | 2025-08
2025-08-30 19:00 | flat_start_nr | 119.52 | 3 | 550 | 2025-08
2025-08-30 20:00 | flat_start_nr | 118.51 | 3 | 540 | 2025-08
2025-08-30 21:00 | flat_start_nr | 120.03 | 3 | 545 | 2025-08
2025-08-30 22:00 | flat_start_nr | 121.11 | 3 | 544 | 2025-08
2025-08-30 23:00 | flat_start_nr | 118.88 | 4 | 539 | 2025-08
2025-08-31 | flat_start_nr | 121.21 | 3 | 536 | 2025-08
2025-08-31 01:00 | flat_start_nr | 138.86 | 4 | 537 | 2025-08
2025-08-31 02:00 | flat_start_nr | 149.36 | 4 | 539 | 2025-08
2025-08-31 03:00 | flat_start_nr | 144.12 | 3 | 550 | 2025-08
2025-08-31 04:00 | flat_start_nr | 143.29 | 3 | 557 | 2025-08
2025-08-31 05:00 | flat_start_nr | 147.8 | 4 | 549 | 2025-08
2025-08-31 19:00 | flat_start_nr | 143.54 | 3 | 566 | 2025-08
2025-08-31 20:00 | flat_start_nr | 132.57 | 3 | 560 | 2025-08
2025-08-31 21:00 | flat_start_nr | 139.71 | 3 | 545 | 2025-08
2025-08-31 22:00 | flat_start_nr | 134.89 | 3 | 555 | 2025-08
2025-08-31 23:00 | flat_start_nr | 137.94 | 3 | 541 | 2025-08
2025-09-01 | flat_start_nr | 143.38 | 3 | 545 | 2025-09
2025-09-01 01:00 | flat_start_nr | 153.6 | 5 | 521 | 2025-09
2025-09-01 02:00 | flat_start_nr | 148.34 | 4 | 526 | 2025-09
2025-09-01 03:00 | flat_start_nr | 143.96 | 3 | 541 | 2025-09
2025-09-01 04:00 | flat_start_nr | 142.07 | 3 | 539 | 2025-09
2025-09-01 05:00 | flat_start_nr | 146.83 | 4 | 524 | 2025-09
2025-09-01 11:00 | flat_start_nr | 154.42 | 5 | 530 | 2025-09
2025-09-01 13:00 | flat_start_nr | 150.42 | 5 | 516 | 2025-09
2025-09-01 14:00 | flat_start_nr | 147.66 | 4 | 525 | 2025-09
2025-09-01 15:00 | flat_start_nr | 144.15 | 3 | 540 | 2025-09
2025-09-01 16:00 | flat_start_nr | 150.28 | 5 | 520 | 2025-09
2025-09-01 17:00 | flat_start_nr | 150.41 | 5 | 527 | 2025-09
2025-09-01 18:00 | flat_start_nr | 151.25 | 5 | 543 | 2025-09
2025-09-01 19:00 | flat_start_nr | 133.97 | 3 | 556 | 2025-09
2025-09-01 20:00 | flat_start_nr | 129.86 | 3 | 555 | 2025-09
2025-09-01 21:00 | flat_start_nr | 151.86 | 5 | 562 | 2025-09
2025-09-02 05:00 | flat_start_nr | 154.84 | 5 | 570 | 2025-09
2025-09-03 10:00 | flat_start_nr | 144.39 | 3 | 551 | 2025-09
2025-09-03 11:00 | flat_start_nr | 144.87 | 3 | 553 | 2025-09
2025-09-03 14:00 | flat_start_nr | 151.42 | 5 | 533 | 2025-09
2025-09-03 19:00 | flat_start_nr | 150.18 | 4 | 532 | 2025-09
2025-09-03 20:00 | flat_start_nr | 154.21 | 5 | 518 | 2025-09
2025-09-04 05:00 | flat_start_nr | 155.9 | 6 | 515 | 2025-09
2025-09-04 06:00 | flat_start_nr | 141.5 | 4 | 541 | 2025-09
2025-09-04 07:00 | flat_start_nr | 152.62 | 5 | 528 | 2025-09
2025-09-04 12:00 | normal_nr | 161.47 | 7 | 542 | 2025-09
2025-09-04 15:00 | normal_nr | 159.98 | 9 | 535 | 2025-09
2025-09-04 18:00 | flat_start_nr | 138.11 | 4 | 552 | 2025-09
2025-09-04 19:00 | flat_start_nr | 120.05 | 3 | 549 | 2025-09
2025-09-04 20:00 | flat_start_nr | 120.8 | 3 | 548 | 2025-09
2025-09-04 21:00 | flat_start_nr | 128.4 | 3 | 540 | 2025-09
2025-09-04 22:00 | flat_start_nr | 128.37 | 3 | 540 | 2025-09
2025-09-04 23:00 | flat_start_nr | 127.81 | 3 | 540 | 2025-09
2025-09-05 | flat_start_nr | 127.49 | 3 | 539 | 2025-09
2025-09-05 01:00 | flat_start_nr | 130.88 | 4 | 536 | 2025-09
2025-09-05 02:00 | flat_start_nr | 125.37 | 3 | 535 | 2025-09
2025-09-05 03:00 | flat_start_nr | 127.67 | 3 | 539 | 2025-09
2025-09-05 04:00 | flat_start_nr | 127.5 | 3 | 539 | 2025-09
2025-09-05 05:00 | flat_start_nr | 127.39 | 3 | 540 | 2025-09
2025-09-05 06:00 | flat_start_nr | 128.94 | 3 | 540 | 2025-09
2025-09-05 07:00 | flat_start_nr | 126.44 | 3 | 545 | 2025-09
2025-09-05 08:00 | flat_start_nr | 148.54 | 5 | 528 | 2025-09
2025-09-05 09:00 | flat_start_nr | 151.53 | 6 | 519 | 2025-09
2025-09-05 10:00 | flat_start_nr | 145.61 | 5 | 531 | 2025-09
2025-09-05 11:00 | flat_start_nr | 141.4 | 4 | 538 | 2025-09
2025-09-05 12:00 | flat_start_nr | 133.7 | 4 | 532 | 2025-09
2025-09-05 13:00 | flat_start_nr | 127.64 | 3 | 532 | 2025-09
2025-09-05 14:00 | flat_start_nr | 128.76 | 3 | 530 | 2025-09
2025-09-05 15:00 | flat_start_nr | 130.7 | 4 | 532 | 2025-09
2025-09-05 16:00 | flat_start_nr | 136.8 | 4 | 539 | 2025-09
2025-09-05 17:00 | flat_start_nr | 137.28 | 3 | 559 | 2025-09
2025-09-05 18:00 | flat_start_nr | 141.76 | 3 | 556 | 2025-09
2025-09-05 19:00 | flat_start_nr | 126.34 | 3 | 555 | 2025-09
2025-09-05 20:00 | flat_start_nr | 137.17 | 4 | 537 | 2025-09
2025-09-05 21:00 | flat_start_nr | 138.08 | 4 | 537 | 2025-09
2025-09-05 22:00 | flat_start_nr | 139.56 | 5 | 539 | 2025-09
2025-09-05 23:00 | flat_start_nr | 154.34 | 7 | 523 | 2025-09
2025-09-06 01:00 | normal_nr | 161.05 | 7 | 554 | 2025-09
2025-09-06 02:00 | flat_start_nr | 147.54 | 6 | 540 | 2025-09
2025-09-06 03:00 | flat_start_nr | 139.43 | 5 | 544 | 2025-09
2025-09-06 04:00 | flat_start_nr | 133.01 | 5 | 539 | 2025-09
2025-09-06 05:00 | flat_start_nr | 122.3 | 4 | 540 | 2025-09
2025-09-06 06:00 | flat_start_nr | 143.63 | 4 | 543 | 2025-09
2025-09-06 07:00 | flat_start_nr | 143.29 | 4 | 547 | 2025-09
2025-09-06 08:00 | flat_start_nr | 140.05 | 4 | 551 | 2025-09
2025-09-06 09:00 | flat_start_nr | 139.39 | 4 | 541 | 2025-09
2025-09-06 10:00 | flat_start_nr | 141.29 | 4 | 550 | 2025-09
2025-09-06 11:00 | flat_start_nr | 140.34 | 4 | 542 | 2025-09
2025-09-06 12:00 | flat_start_nr | 138.62 | 4 | 540 | 2025-09
2025-09-06 13:00 | flat_start_nr | 134.59 | 4 | 541 | 2025-09
2025-09-06 14:00 | flat_start_nr | 124.38 | 3 | 537 | 2025-09
2025-09-06 15:00 | flat_start_nr | 123.92 | 3 | 540 | 2025-09
2025-09-06 16:00 | flat_start_nr | 120.7 | 3 | 543 | 2025-09
2025-09-06 17:00 | flat_start_nr | 122.88 | 3 | 548 | 2025-09
2025-09-06 18:00 | flat_start_nr | 126.69 | 3 | 541 | 2025-09
2025-09-06 19:00 | flat_start_nr | 117.69 | 3 | 541 | 2025-09
2025-09-06 20:00 | flat_start_nr | 140.21 | 5 | 553 | 2025-09
2025-09-06 21:00 | flat_start_nr | 133.91 | 5 | 546 | 2025-09
2025-09-06 22:00 | flat_start_nr | 131.62 | 5 | 541 | 2025-09
2025-09-06 23:00 | flat_start_nr | 129.39 | 4 | 545 | 2025-09
2025-09-07 | flat_start_nr | 130.64 | 5 | 544 | 2025-09
2025-09-07 01:00 | flat_start_nr | 124.02 | 4 | 545 | 2025-09
2025-09-07 02:00 | flat_start_nr | 126.29 | 4 | 545 | 2025-09
2025-09-07 03:00 | flat_start_nr | 121.34 | 4 | 536 | 2025-09
2025-09-07 04:00 | flat_start_nr | 118.15 | 4 | 538 | 2025-09
2025-09-07 05:00 | flat_start_nr | 120.42 | 4 | 537 | 2025-09
2025-09-07 06:00 | flat_start_nr | 138.76 | 4 | 536 | 2025-09
2025-09-07 07:00 | flat_start_nr | 154.33 | 6 | 550 | 2025-09
2025-09-07 08:00 | flat_start_nr | 148.73 | 5 | 532 | 2025-09
2025-09-07 09:00 | flat_start_nr | 141.76 | 4 | 542 | 2025-09
2025-09-07 10:00 | flat_start_nr | 142.1 | 4 | 542 | 2025-09
2025-09-07 11:00 | flat_start_nr | 138.86 | 4 | 540 | 2025-09
2025-09-07 12:00 | flat_start_nr | 127 | 3 | 534 | 2025-09
2025-09-07 13:00 | flat_start_nr | 120.14 | 3 | 540 | 2025-09
2025-09-07 14:00 | flat_start_nr | 133.65 | 4 | 541 | 2025-09
2025-09-07 15:00 | flat_start_nr | 144.63 | 4 | 525 | 2025-09
2025-09-07 16:00 | flat_start_nr | 134.95 | 4 | 534 | 2025-09
2025-09-07 17:00 | flat_start_nr | 130.09 | 4 | 547 | 2025-09
2025-09-07 18:00 | flat_start_nr | 130.19 | 4 | 537 | 2025-09
2025-09-07 19:00 | flat_start_nr | 114.89 | 2 | 550 | 2025-09
2025-09-07 20:00 | flat_start_nr | 115.52 | 2 | 549 | 2025-09
2025-09-07 21:00 | flat_start_nr | 120.75 | 3 | 547 | 2025-09
2025-09-07 22:00 | flat_start_nr | 154.22 | 6 | 552 | 2025-09
2025-09-08 | flat_start_nr | 156.89 | 7 | 538 | 2025-09
2025-09-08 01:00 | flat_start_nr | 157.98 | 7 | 537 | 2025-09
2025-09-08 02:00 | flat_start_nr | 148.01 | 6 | 528 | 2025-09
2025-09-08 03:00 | flat_start_nr | 154.01 | 6 | 517 | 2025-09
2025-09-08 04:00 | flat_start_nr | 142.64 | 4 | 543 | 2025-09
2025-09-08 05:00 | flat_start_nr | 143.97 | 4 | 550 | 2025-09
2025-09-08 06:00 | flat_start_nr | 146.07 | 5 | 545 | 2025-09
2025-09-08 08:00 | flat_start_nr | 149.5 | 6 | 522 | 2025-09
2025-09-08 09:00 | flat_start_nr | 154.06 | 5 | 552 | 2025-09
2025-09-08 11:00 | flat_start_nr | 154.15 | 5 | 570 | 2025-09
2025-09-08 12:00 | flat_start_nr | 154.31 | 5 | 568 | 2025-09
2025-09-08 14:00 | flat_start_nr | 151.25 | 5 | 529 | 2025-09
2025-09-08 15:00 | flat_start_nr | 152.89 | 6 | 550 | 2025-09
2025-09-08 16:00 | flat_start_nr | 129.71 | 4 | 552 | 2025-09
2025-09-08 17:00 | flat_start_nr | 123.72 | 3 | 555 | 2025-09
2025-09-08 18:00 | flat_start_nr | 124.8 | 3 | 552 | 2025-09
2025-09-08 19:00 | flat_start_nr | 116.2 | 2 | 560 | 2025-09
2025-09-08 20:00 | flat_start_nr | 121.48 | 3 | 556 | 2025-09
2025-09-08 21:00 | flat_start_nr | 143.74 | 3 | 569 | 2025-09
2025-09-09 | flat_start_nr | 144.39 | 4 | 538 | 2025-09
2025-09-09 01:00 | flat_start_nr | 155.76 | 6 | 544 | 2025-09
2025-09-09 04:00 | flat_start_nr | 154.82 | 6 | 520 | 2025-09
2025-09-09 05:00 | flat_start_nr | 138.23 | 5 | 546 | 2025-09
2025-09-09 06:00 | flat_start_nr | 148.16 | 5 | 533 | 2025-09
2025-09-09 10:00 | flat_start_nr | 154 | 6 | 535 | 2025-09
2025-09-09 11:00 | flat_start_nr | 155.56 | 6 | 526 | 2025-09
2025-09-09 12:00 | flat_start_nr | 146.29 | 5 | 533 | 2025-09
2025-09-09 13:00 | flat_start_nr | 142.06 | 4 | 551 | 2025-09
2025-09-09 14:00 | flat_start_nr | 151.39 | 6 | 539 | 2025-09
2025-09-09 15:00 | flat_start_nr | 136.81 | 4 | 548 | 2025-09
2025-09-09 16:00 | flat_start_nr | 130.41 | 4 | 540 | 2025-09
2025-09-09 17:00 | flat_start_nr | 127.39 | 3 | 544 | 2025-09
2025-09-09 18:00 | flat_start_nr | 134.81 | 4 | 540 | 2025-09
2025-09-09 19:00 | flat_start_nr | 130.57 | 4 | 536 | 2025-09
2025-09-09 20:00 | flat_start_nr | 136.98 | 5 | 536 | 2025-09
2025-09-09 21:00 | flat_start_nr | 139.89 | 4 | 541 | 2025-09
2025-09-09 22:00 | flat_start_nr | 155.34 | 6 | 552 | 2025-09
2025-09-09 23:00 | flat_start_nr | 150.95 | 5 | 535 | 2025-09
2025-09-10 | flat_start_nr | 145.08 | 4 | 540 | 2025-09
2025-09-10 01:00 | flat_start_nr | 145.86 | 5 | 537 | 2025-09
2025-09-10 02:00 | flat_start_nr | 147.44 | 6 | 534 | 2025-09
2025-09-10 03:00 | flat_start_nr | 144.25 | 5 | 536 | 2025-09
2025-09-10 04:00 | flat_start_nr | 134.63 | 5 | 537 | 2025-09
2025-09-10 05:00 | flat_start_nr | 123.88 | 3 | 537 | 2025-09
2025-09-10 06:00 | flat_start_nr | 129.7 | 4 | 540 | 2025-09
2025-09-10 07:00 | flat_start_nr | 122.48 | 3 | 540 | 2025-09
2025-09-10 08:00 | flat_start_nr | 124.26 | 3 | 533 | 2025-09
2025-09-10 09:00 | flat_start_nr | 120.52 | 3 | 537 | 2025-09
2025-09-10 10:00 | flat_start_nr | 125.71 | 3 | 530 | 2025-09
2025-09-10 11:00 | flat_start_nr | 121.96 | 3 | 539 | 2025-09
2025-09-10 12:00 | flat_start_nr | 127.59 | 3 | 537 | 2025-09
2025-09-10 13:00 | flat_start_nr | 123.92 | 3 | 534 | 2025-09
2025-09-10 14:00 | flat_start_nr | 126.69 | 2 | 544 | 2025-09
2025-09-10 15:00 | flat_start_nr | 133.33 | 3 | 539 | 2025-09
2025-09-10 16:00 | flat_start_nr | 131.72 | 3 | 545 | 2025-09
2025-09-10 17:00 | flat_start_nr | 139.58 | 3 | 548 | 2025-09
2025-09-10 18:00 | flat_start_nr | 138.79 | 3 | 551 | 2025-09
2025-09-10 19:00 | flat_start_nr | 123.48 | 2 | 547 | 2025-09
2025-09-10 20:00 | flat_start_nr | 123.38 | 2 | 552 | 2025-09
2025-09-10 21:00 | flat_start_nr | 117.99 | 4 | 536 | 2025-09
2025-09-10 22:00 | flat_start_nr | 130.24 | 4 | 529 | 2025-09
2025-09-10 23:00 | flat_start_nr | 117.77 | 3 | 541 | 2025-09
2025-09-11 | flat_start_nr | 121 | 3 | 537 | 2025-09
2025-09-11 01:00 | flat_start_nr | 126.98 | 3 | 537 | 2025-09
2025-09-11 02:00 | flat_start_nr | 133.28 | 4 | 528 | 2025-09
2025-09-11 03:00 | flat_start_nr | 125.75 | 3 | 532 | 2025-09
2025-09-11 04:00 | flat_start_nr | 123.26 | 3 | 537 | 2025-09
2025-09-11 05:00 | flat_start_nr | 122.05 | 3 | 535 | 2025-09
2025-09-11 06:00 | flat_start_nr | 136.89 | 4 | 535 | 2025-09
2025-09-11 09:00 | flat_start_nr | 153.09 | 6 | 541 | 2025-09
2025-09-11 10:00 | flat_start_nr | 129.22 | 3 | 525 | 2025-09
2025-09-11 11:00 | flat_start_nr | 118.32 | 3 | 530 | 2025-09
2025-09-11 12:00 | flat_start_nr | 118.12 | 2 | 534 | 2025-09
2025-09-11 13:00 | flat_start_nr | 118.32 | 2 | 541 | 2025-09
2025-09-11 14:00 | flat_start_nr | 115.26 | 2 | 539 | 2025-09
2025-09-11 15:00 | flat_start_nr | 118.58 | 3 | 531 | 2025-09
2025-09-11 16:00 | flat_start_nr | 133.44 | 4 | 538 | 2025-09
2025-09-11 17:00 | flat_start_nr | 118.64 | 3 | 536 | 2025-09
2025-09-11 18:00 | flat_start_nr | 114.23 | 2 | 540 | 2025-09
2025-09-11 19:00 | flat_start_nr | 114.14 | 2 | 544 | 2025-09
2025-09-11 20:00 | flat_start_nr | 114.7 | 2 | 541 | 2025-09
2025-09-11 21:00 | flat_start_nr | 133.76 | 3 | 548 | 2025-09
2025-09-11 22:00 | flat_start_nr | 147.19 | 4 | 535 | 2025-09
2025-09-11 23:00 | flat_start_nr | 130.43 | 4 | 544 | 2025-09
2025-09-12 | flat_start_nr | 125.71 | 3 | 541 | 2025-09
2025-09-12 01:00 | flat_start_nr | 129.09 | 3 | 535 | 2025-09
2025-09-12 02:00 | flat_start_nr | 124.82 | 3 | 536 | 2025-09
2025-09-12 03:00 | flat_start_nr | 123.62 | 3 | 538 | 2025-09
2025-09-12 04:00 | flat_start_nr | 126.5 | 4 | 534 | 2025-09
2025-09-12 05:00 | flat_start_nr | 124.86 | 4 | 538 | 2025-09
2025-09-12 06:00 | flat_start_nr | 131.11 | 5 | 531 | 2025-09
2025-09-12 07:00 | flat_start_nr | 134.41 | 4 | 530 | 2025-09
2025-09-12 08:00 | flat_start_nr | 140.01 | 4 | 540 | 2025-09
2025-09-12 09:00 | flat_start_nr | 133.83 | 4 | 530 | 2025-09
2025-09-12 10:00 | flat_start_nr | 133.17 | 4 | 527 | 2025-09
2025-09-12 11:00 | flat_start_nr | 137.43 | 4 | 525 | 2025-09
2025-09-12 12:00 | flat_start_nr | 132.64 | 4 | 526 | 2025-09
2025-09-12 13:00 | flat_start_nr | 124.47 | 4 | 526 | 2025-09
2025-09-12 14:00 | flat_start_nr | 136.5 | 4 | 525 | 2025-09
2025-09-12 15:00 | flat_start_nr | 146.49 | 5 | 512 | 2025-09
2025-09-12 16:00 | flat_start_nr | 143.81 | 3 | 535 | 2025-09
2025-09-12 17:00 | flat_start_nr | 136.92 | 3 | 545 | 2025-09
2025-09-12 18:00 | flat_start_nr | 136.08 | 3 | 544 | 2025-09
2025-09-12 19:00 | flat_start_nr | 109.93 | 2 | 529 | 2025-09
2025-09-12 20:00 | flat_start_nr | 121 | 4 | 529 | 2025-09
2025-09-12 21:00 | flat_start_nr | 125.97 | 4 | 535 | 2025-09
2025-09-12 22:00 | flat_start_nr | 134.73 | 4 | 539 | 2025-09
2025-09-12 23:00 | flat_start_nr | 121.14 | 4 | 539 | 2025-09
2025-09-13 | flat_start_nr | 120.19 | 4 | 534 | 2025-09
2025-09-13 01:00 | flat_start_nr | 118.24 | 4 | 532 | 2025-09
2025-09-13 02:00 | flat_start_nr | 128.87 | 4 | 534 | 2025-09
2025-09-13 03:00 | flat_start_nr | 122.37 | 4 | 532 | 2025-09
2025-09-13 04:00 | flat_start_nr | 117.9 | 4 | 535 | 2025-09
2025-09-13 05:00 | flat_start_nr | 116.7 | 4 | 533 | 2025-09
2025-09-13 06:00 | flat_start_nr | 132.93 | 5 | 534 | 2025-09
2025-09-13 07:00 | flat_start_nr | 126.67 | 4 | 539 | 2025-09
2025-09-13 08:00 | flat_start_nr | 131.41 | 4 | 537 | 2025-09
2025-09-13 09:00 | flat_start_nr | 132.1 | 4 | 532 | 2025-09
2025-09-13 10:00 | flat_start_nr | 127.18 | 3 | 527 | 2025-09
2025-09-13 11:00 | flat_start_nr | 123.7 | 3 | 527 | 2025-09
2025-09-13 12:00 | flat_start_nr | 119.37 | 3 | 536 | 2025-09
2025-09-13 13:00 | flat_start_nr | 119.07 | 3 | 540 | 2025-09
2025-09-13 14:00 | flat_start_nr | 120.08 | 3 | 539 | 2025-09
2025-09-13 15:00 | flat_start_nr | 127.16 | 3 | 529 | 2025-09
2025-09-13 16:00 | flat_start_nr | 135.75 | 3 | 536 | 2025-09
2025-09-13 17:00 | flat_start_nr | 143.16 | 3 | 529 | 2025-09
2025-09-13 18:00 | flat_start_nr | 145.61 | 3 | 535 | 2025-09
2025-09-13 19:00 | flat_start_nr | 128.42 | 2 | 540 | 2025-09
2025-09-13 20:00 | flat_start_nr | 131.58 | 3 | 544 | 2025-09
2025-09-13 21:00 | flat_start_nr | 118.78 | 3 | 542 | 2025-09
2025-09-13 22:00 | flat_start_nr | 125.28 | 3 | 537 | 2025-09
2025-09-13 23:00 | flat_start_nr | 123.06 | 4 | 543 | 2025-09
2025-09-14 | flat_start_nr | 130.18 | 4 | 540 | 2025-09
2025-09-14 01:00 | flat_start_nr | 140.19 | 4 | 537 | 2025-09
2025-09-14 02:00 | flat_start_nr | 141.57 | 4 | 539 | 2025-09
2025-09-14 03:00 | flat_start_nr | 143.36 | 4 | 540 | 2025-09
2025-09-14 04:00 | flat_start_nr | 137.69 | 4 | 530 | 2025-09
2025-09-14 05:00 | flat_start_nr | 139.43 | 6 | 537 | 2025-09
2025-09-14 08:00 | flat_start_nr | 154.22 | 6 | 520 | 2025-09
2025-09-14 09:00 | flat_start_nr | 153.2 | 6 | 538 | 2025-09
2025-09-14 10:00 | flat_start_nr | 155 | 6 | 523 | 2025-09
2025-09-14 12:00 | flat_start_nr | 148.72 | 5 | 513 | 2025-09
2025-09-14 13:00 | flat_start_nr | 137.46 | 4 | 537 | 2025-09
2025-09-14 14:00 | flat_start_nr | 127.56 | 3 | 538 | 2025-09
2025-09-14 15:00 | flat_start_nr | 121.81 | 3 | 545 | 2025-09
2025-09-14 16:00 | flat_start_nr | 122.79 | 3 | 537 | 2025-09
2025-09-14 17:00 | flat_start_nr | 127.99 | 3 | 536 | 2025-09
2025-09-14 18:00 | flat_start_nr | 130.44 | 5 | 531 | 2025-09
2025-09-14 19:00 | flat_start_nr | 113.65 | 3 | 542 | 2025-09
2025-09-14 20:00 | flat_start_nr | 121.13 | 3 | 536 | 2025-09
2025-09-14 21:00 | flat_start_nr | 131.77 | 4 | 534 | 2025-09
2025-09-14 22:00 | flat_start_nr | 141.65 | 5 | 532 | 2025-09
2025-09-14 23:00 | flat_start_nr | 146.71 | 5 | 531 | 2025-09
2025-09-15 | flat_start_nr | 147.92 | 5 | 521 | 2025-09
2025-09-15 01:00 | flat_start_nr | 150.27 | 5 | 518 | 2025-09
2025-09-15 02:00 | flat_start_nr | 150.31 | 5 | 521 | 2025-09
2025-09-15 03:00 | flat_start_nr | 151.32 | 5 | 524 | 2025-09
2025-09-15 04:00 | flat_start_nr | 151.04 | 5 | 525 | 2025-09
2025-09-15 05:00 | flat_start_nr | 141.74 | 4 | 538 | 2025-09
2025-09-15 08:00 | flat_start_nr | 142.05 | 4 | 539 | 2025-09
2025-09-15 09:00 | flat_start_nr | 147.04 | 5 | 523 | 2025-09
2025-09-15 12:00 | flat_start_nr | 145.69 | 5 | 525 | 2025-09
2025-09-15 13:00 | flat_start_nr | 136.59 | 4 | 544 | 2025-09
2025-09-15 14:00 | flat_start_nr | 148.31 | 5 | 524 | 2025-09
2025-09-15 17:00 | flat_start_nr | 148.85 | 5 | 517 | 2025-09
2025-09-15 18:00 | flat_start_nr | 123.82 | 4 | 543 | 2025-09
2025-09-15 19:00 | flat_start_nr | 115.21 | 3 | 548 | 2025-09
2025-09-15 20:00 | flat_start_nr | 116.65 | 3 | 544 | 2025-09
2025-09-15 21:00 | flat_start_nr | 151.36 | 4 | 529 | 2025-09
2025-09-15 22:00 | flat_start_nr | 150.94 | 4 | 533 | 2025-09
2025-09-15 23:00 | flat_start_nr | 141.96 | 3 | 552 | 2025-09
2025-09-16 | flat_start_nr | 141.87 | 3 | 555 | 2025-09
2025-09-16 01:00 | flat_start_nr | 135.57 | 3 | 548 | 2025-09
2025-09-16 02:00 | flat_start_nr | 124.49 | 3 | 547 | 2025-09
2025-09-16 03:00 | flat_start_nr | 122.44 | 4 | 538 | 2025-09
2025-09-16 04:00 | flat_start_nr | 120.6 | 4 | 542 | 2025-09
2025-09-16 05:00 | flat_start_nr | 132.17 | 5 | 537 | 2025-09
2025-09-16 06:00 | flat_start_nr | 135.17 | 5 | 533 | 2025-09
2025-09-16 07:00 | flat_start_nr | 133.76 | 5 | 551 | 2025-09
2025-09-16 08:00 | flat_start_nr | 146.73 | 5 | 525 | 2025-09
2025-09-16 09:00 | flat_start_nr | 134.49 | 4 | 535 | 2025-09
2025-09-16 10:00 | flat_start_nr | 128.51 | 3 | 537 | 2025-09
2025-09-16 11:00 | flat_start_nr | 122.31 | 4 | 542 | 2025-09
2025-09-16 12:00 | flat_start_nr | 125.55 | 3 | 541 | 2025-09
2025-09-16 13:00 | flat_start_nr | 126.01 | 3 | 540 | 2025-09
2025-09-16 14:00 | flat_start_nr | 130.59 | 4 | 542 | 2025-09
2025-09-16 15:00 | flat_start_nr | 131.11 | 4 | 543 | 2025-09
2025-09-16 16:00 | flat_start_nr | 137.28 | 4 | 540 | 2025-09
2025-09-16 17:00 | flat_start_nr | 122.54 | 3 | 546 | 2025-09
2025-09-16 18:00 | flat_start_nr | 125.03 | 3 | 539 | 2025-09
2025-09-16 19:00 | flat_start_nr | 116.49 | 4 | 542 | 2025-09
2025-09-16 20:00 | flat_start_nr | 135.02 | 4 | 544 | 2025-09
2025-09-16 21:00 | flat_start_nr | 138.28 | 4 | 538 | 2025-09
2025-09-16 22:00 | flat_start_nr | 152.65 | 6 | 545 | 2025-09
2025-09-16 23:00 | flat_start_nr | 154.9 | 6 | 552 | 2025-09
2025-09-17 04:00 | flat_start_nr | 155.53 | 6 | 554 | 2025-09
2025-09-17 05:00 | flat_start_nr | 134.9 | 4 | 546 | 2025-09
2025-09-17 06:00 | flat_start_nr | 136.73 | 4 | 542 | 2025-09
2025-09-17 09:00 | flat_start_nr | 146.4 | 5 | 520 | 2025-09
2025-09-17 10:00 | flat_start_nr | 142.41 | 4 | 531 | 2025-09
2025-09-17 11:00 | flat_start_nr | 143.45 | 4 | 535 | 2025-09
2025-09-17 12:00 | flat_start_nr | 140.33 | 4 | 536 | 2025-09
2025-09-17 13:00 | flat_start_nr | 135.03 | 4 | 534 | 2025-09
2025-09-17 14:00 | flat_start_nr | 129.08 | 3 | 534 | 2025-09
2025-09-17 15:00 | flat_start_nr | 128.54 | 3 | 539 | 2025-09
2025-09-17 16:00 | flat_start_nr | 133.56 | 4 | 538 | 2025-09
2025-09-17 17:00 | flat_start_nr | 125.74 | 3 | 545 | 2025-09
2025-09-17 18:00 | flat_start_nr | 132.34 | 4 | 543 | 2025-09
2025-09-17 19:00 | flat_start_nr | 144.1 | 4 | 537 | 2025-09
2025-09-17 20:00 | flat_start_nr | 155.45 | 6 | 525 | 2025-09
2025-09-17 21:00 | normal_nr | 160.65 | 6 | 546 | 2025-09
2025-09-17 22:00 | flat_start_nr | 155.32 | 6 | 524 | 2025-09
2025-09-18 04:00 | flat_start_nr | 157.39 | 6 | 549 | 2025-09
2025-09-18 05:00 | flat_start_nr | 145.96 | 5 | 538 | 2025-09
2025-09-18 08:00 | flat_start_nr | 149.87 | 5 | 520 | 2025-09
2025-09-18 09:00 | flat_start_nr | 146.14 | 5 | 523 | 2025-09
2025-09-18 10:00 | flat_start_nr | 141.25 | 4 | 540 | 2025-09
2025-09-18 11:00 | flat_start_nr | 134.16 | 4 | 532 | 2025-09
2025-09-18 12:00 | flat_start_nr | 134.51 | 4 | 532 | 2025-09
2025-09-18 13:00 | flat_start_nr | 137.96 | 4 | 518 | 2025-09
2025-09-18 14:00 | flat_start_nr | 147.15 | 5 | 505 | 2025-09
2025-09-18 15:00 | flat_start_nr | 148.15 | 5 | 511 | 2025-09
2025-09-18 16:00 | flat_start_nr | 134.3 | 4 | 534 | 2025-09
2025-09-18 17:00 | flat_start_nr | 138.19 | 5 | 536 | 2025-09
2025-09-18 18:00 | flat_start_nr | 146.2 | 6 | 512 | 2025-09
2025-09-18 19:00 | flat_start_nr | 128.35 | 3 | 538 | 2025-09
2025-09-18 20:00 | flat_start_nr | 147.93 | 5 | 531 | 2025-09
2025-09-18 21:00 | flat_start_nr | 134.14 | 4 | 535 | 2025-09
2025-09-18 22:00 | flat_start_nr | 126.14 | 3 | 536 | 2025-09
2025-09-18 23:00 | flat_start_nr | 117.22 | 2 | 536 | 2025-09
2025-09-19 | flat_start_nr | 116.8 | 2 | 538 | 2025-09
2025-09-19 01:00 | flat_start_nr | 116.99 | 2 | 531 | 2025-09
2025-09-19 02:00 | flat_start_nr | 125.51 | 3 | 531 | 2025-09
2025-09-19 03:00 | flat_start_nr | 125.86 | 3 | 532 | 2025-09
2025-09-19 04:00 | flat_start_nr | 124.35 | 4 | 536 | 2025-09
2025-09-19 05:00 | flat_start_nr | 119.14 | 4 | 537 | 2025-09
2025-09-19 06:00 | flat_start_nr | 125.05 | 4 | 535 | 2025-09
2025-09-19 07:00 | flat_start_nr | 123.6 | 4 | 541 | 2025-09
2025-09-19 08:00 | flat_start_nr | 135.61 | 4 | 532 | 2025-09
2025-09-19 09:00 | flat_start_nr | 138.44 | 4 | 532 | 2025-09
2025-09-19 10:00 | flat_start_nr | 133.94 | 4 | 530 | 2025-09
2025-09-19 11:00 | flat_start_nr | 122.8 | 4 | 542 | 2025-09
2025-09-19 12:00 | flat_start_nr | 122.23 | 4 | 542 | 2025-09
2025-09-19 13:00 | flat_start_nr | 122.4 | 4 | 542 | 2025-09
2025-09-19 14:00 | flat_start_nr | 119.93 | 4 | 543 | 2025-09
2025-09-19 15:00 | flat_start_nr | 130.56 | 4 | 551 | 2025-09
2025-09-19 16:00 | flat_start_nr | 141.81 | 4 | 542 | 2025-09
2025-09-19 17:00 | flat_start_nr | 121.31 | 3 | 543 | 2025-09
2025-09-19 18:00 | flat_start_nr | 112.69 | 2 | 545 | 2025-09
2025-09-19 19:00 | flat_start_nr | 113.34 | 3 | 545 | 2025-09
2025-09-19 20:00 | flat_start_nr | 133.48 | 3 | 551 | 2025-09
2025-09-19 21:00 | flat_start_nr | 128.65 | 3 | 547 | 2025-09
2025-09-19 22:00 | flat_start_nr | 134.53 | 4 | 539 | 2025-09
2025-09-19 23:00 | flat_start_nr | 132.94 | 5 | 537 | 2025-09
2025-09-20 | flat_start_nr | 143.85 | 4 | 536 | 2025-09
2025-09-20 01:00 | flat_start_nr | 140.44 | 4 | 540 | 2025-09
2025-09-20 02:00 | flat_start_nr | 140.32 | 4 | 540 | 2025-09
2025-09-20 03:00 | flat_start_nr | 150.17 | 5 | 530 | 2025-09
2025-09-20 04:00 | flat_start_nr | 149.32 | 5 | 530 | 2025-09
2025-09-20 05:00 | flat_start_nr | 141.22 | 5 | 540 | 2025-09
2025-09-20 15:00 | flat_start_nr | 144.59 | 4 | 533 | 2025-09
2025-09-20 16:00 | flat_start_nr | 142.39 | 4 | 543 | 2025-09
2025-09-20 17:00 | flat_start_nr | 138.41 | 4 | 545 | 2025-09
2025-09-20 18:00 | flat_start_nr | 135.53 | 4 | 540 | 2025-09
2025-09-20 19:00 | flat_start_nr | 125.88 | 4 | 541 | 2025-09
2025-09-20 20:00 | flat_start_nr | 146.17 | 6 | 539 | 2025-09
2025-09-20 21:00 | flat_start_nr | 156.35 | 7 | 521 | 2025-09
2025-09-20 22:00 | flat_start_nr | 147.75 | 6 | 539 | 2025-09
2025-09-20 23:00 | flat_start_nr | 152.74 | 7 | 521 | 2025-09
2025-09-21 | flat_start_nr | 157.59 | 7 | 547 | 2025-09
2025-09-21 18:00 | flat_start_nr | 152.45 | 7 | 520 | 2025-09
2025-09-21 19:00 | flat_start_nr | 147.69 | 6 | 527 | 2025-09
2025-09-21 20:00 | normal_nr | 161.59 | 7 | 546 | 2025-09
2025-09-22 03:00 | flat_start_nr | 156.82 | 7 | 557 | 2025-09
2025-09-22 04:00 | flat_start_nr | 153.91 | 6 | 537 | 2025-09
2025-09-22 05:00 | flat_start_nr | 135 | 4 | 548 | 2025-09
2025-09-22 06:00 | flat_start_nr | 127.12 | 4 | 544 | 2025-09
2025-09-22 07:00 | flat_start_nr | 131.03 | 5 | 542 | 2025-09
2025-09-22 08:00 | flat_start_nr | 133.16 | 5 | 541 | 2025-09
2025-09-22 09:00 | flat_start_nr | 121.59 | 4 | 535 | 2025-09
2025-09-22 10:00 | flat_start_nr | 131.86 | 4 | 528 | 2025-09
2025-09-22 11:00 | flat_start_nr | 128.97 | 3 | 527 | 2025-09
2025-09-22 12:00 | flat_start_nr | 127.61 | 3 | 528 | 2025-09
2025-09-22 13:00 | flat_start_nr | 140.28 | 4 | 533 | 2025-09
2025-09-22 14:00 | flat_start_nr | 147.97 | 5 | 531 | 2025-09
2025-09-22 15:00 | flat_start_nr | 147.63 | 4 | 530 | 2025-09
2025-09-22 16:00 | flat_start_nr | 151.19 | 5 | 538 | 2025-09
2025-09-22 17:00 | flat_start_nr | 147.95 | 4 | 518 | 2025-09
2025-09-22 18:00 | flat_start_nr | 146.59 | 4 | 535 | 2025-09
2025-09-22 19:00 | flat_start_nr | 147.5 | 5 | 531 | 2025-09
2025-09-23 11:00 | flat_start_nr | 155.01 | 6 | 533 | 2025-09
2025-09-23 12:00 | flat_start_nr | 145.24 | 4 | 534 | 2025-09
2025-09-23 13:00 | flat_start_nr | 141.74 | 4 | 539 | 2025-09
2025-09-23 14:00 | flat_start_nr | 143.66 | 4 | 532 | 2025-09
2025-09-23 15:00 | flat_start_nr | 137.02 | 4 | 544 | 2025-09
2025-09-23 16:00 | flat_start_nr | 144.56 | 3 | 545 | 2025-09
2025-09-23 17:00 | flat_start_nr | 140.08 | 4 | 545 | 2025-09
2025-09-23 18:00 | flat_start_nr | 136.04 | 4 | 537 | 2025-09
2025-09-23 19:00 | flat_start_nr | 126.52 | 4 | 535 | 2025-09
2025-09-23 20:00 | flat_start_nr | 136.43 | 6 | 531 | 2025-09
2025-09-23 21:00 | flat_start_nr | 148.13 | 6 | 531 | 2025-09
2025-09-23 22:00 | flat_start_nr | 145.54 | 6 | 534 | 2025-09
2025-09-23 23:00 | flat_start_nr | 156.88 | 7 | 536 | 2025-09
2025-09-24 | flat_start_nr | 153.79 | 6 | 522 | 2025-09
2025-09-24 01:00 | flat_start_nr | 155.84 | 6 | 552 | 2025-09
2025-09-24 02:00 | flat_start_nr | 155.5 | 6 | 544 | 2025-09
2025-09-24 03:00 | flat_start_nr | 151.54 | 5 | 526 | 2025-09
2025-09-24 04:00 | flat_start_nr | 148.57 | 5 | 524 | 2025-09
2025-09-24 05:00 | flat_start_nr | 146.04 | 6 | 530 | 2025-09
2025-09-24 06:00 | flat_start_nr | 155.13 | 6 | 545 | 2025-09
2025-09-24 07:00 | flat_start_nr | 153.63 | 6 | 527 | 2025-09
2025-09-24 10:00 | flat_start_nr | 151.68 | 6 | 524 | 2025-09
2025-09-24 11:00 | flat_start_nr | 148.13 | 5 | 523 | 2025-09
2025-09-24 12:00 | flat_start_nr | 146.17 | 5 | 533 | 2025-09
2025-09-24 13:00 | flat_start_nr | 150.66 | 5 | 529 | 2025-09
2025-09-24 14:00 | flat_start_nr | 149.71 | 5 | 534 | 2025-09
2025-09-24 15:00 | flat_start_nr | 147.76 | 5 | 522 | 2025-09
2025-09-24 16:00 | flat_start_nr | 143.56 | 4 | 552 | 2025-09
2025-09-24 17:00 | flat_start_nr | 151.3 | 5 | 529 | 2025-09
2025-09-24 18:00 | flat_start_nr | 129.99 | 4 | 542 | 2025-09
2025-09-24 19:00 | flat_start_nr | 116.41 | 4 | 545 | 2025-09
2025-09-24 20:00 | flat_start_nr | 125.44 | 3 | 543 | 2025-09
2025-09-24 21:00 | flat_start_nr | 126.99 | 3 | 545 | 2025-09
2025-09-24 22:00 | flat_start_nr | 132.2 | 4 | 540 | 2025-09
2025-09-24 23:00 | flat_start_nr | 124.16 | 3 | 539 | 2025-09
2025-09-25 | flat_start_nr | 126.37 | 3 | 537 | 2025-09
2025-09-25 01:00 | flat_start_nr | 134.84 | 5 | 541 | 2025-09
2025-09-25 02:00 | flat_start_nr | 142.39 | 5 | 534 | 2025-09
2025-09-25 03:00 | flat_start_nr | 136.67 | 4 | 538 | 2025-09
2025-09-25 04:00 | flat_start_nr | 125.25 | 3 | 536 | 2025-09
2025-09-25 05:00 | flat_start_nr | 119.72 | 3 | 531 | 2025-09
2025-09-25 06:00 | flat_start_nr | 139.79 | 4 | 528 | 2025-09
2025-09-25 07:00 | flat_start_nr | 143.97 | 4 | 540 | 2025-09
2025-09-25 08:00 | flat_start_nr | 142.82 | 4 | 542 | 2025-09
2025-09-25 09:00 | flat_start_nr | 143.96 | 4 | 542 | 2025-09
2025-09-25 10:00 | flat_start_nr | 142.02 | 4 | 543 | 2025-09
2025-09-25 11:00 | flat_start_nr | 143.3 | 4 | 537 | 2025-09
2025-09-25 12:00 | flat_start_nr | 142.6 | 4 | 540 | 2025-09
2025-09-25 13:00 | flat_start_nr | 144.47 | 4 | 537 | 2025-09
2025-09-25 14:00 | flat_start_nr | 143.12 | 4 | 544 | 2025-09
2025-09-25 15:00 | flat_start_nr | 142.48 | 4 | 543 | 2025-09
2025-09-25 16:00 | flat_start_nr | 141.23 | 4 | 543 | 2025-09
2025-09-25 17:00 | flat_start_nr | 147.98 | 5 | 524 | 2025-09
2025-09-25 18:00 | flat_start_nr | 141.57 | 5 | 549 | 2025-09
2025-09-25 19:00 | flat_start_nr | 134.28 | 6 | 546 | 2025-09
2025-09-25 20:00 | flat_start_nr | 134.89 | 5 | 541 | 2025-09
2025-09-25 21:00 | flat_start_nr | 133.52 | 5 | 536 | 2025-09
2025-09-25 22:00 | flat_start_nr | 139.43 | 4 | 535 | 2025-09
2025-09-25 23:00 | flat_start_nr | 141.48 | 4 | 533 | 2025-09
2025-09-26 | flat_start_nr | 138.71 | 4 | 534 | 2025-09
2025-09-26 01:00 | flat_start_nr | 139.51 | 4 | 535 | 2025-09
2025-09-26 02:00 | flat_start_nr | 139.52 | 4 | 534 | 2025-09
2025-09-26 03:00 | flat_start_nr | 138.34 | 4 | 534 | 2025-09
2025-09-26 04:00 | flat_start_nr | 141.13 | 5 | 537 | 2025-09
2025-09-26 05:00 | flat_start_nr | 129.51 | 3 | 544 | 2025-09
2025-09-26 06:00 | flat_start_nr | 127.17 | 3 | 547 | 2025-09
2025-09-26 07:00 | flat_start_nr | 129.76 | 4 | 546 | 2025-09
2025-09-26 08:00 | flat_start_nr | 141.72 | 4 | 548 | 2025-09
2025-09-26 09:00 | flat_start_nr | 143.35 | 4 | 551 | 2025-09
2025-09-26 10:00 | flat_start_nr | 147.75 | 5 | 542 | 2025-09
2025-09-26 11:00 | flat_start_nr | 149.2 | 5 | 533 | 2025-09
2025-09-26 12:00 | flat_start_nr | 151.91 | 6 | 524 | 2025-09
2025-09-26 13:00 | flat_start_nr | 150.58 | 6 | 529 | 2025-09
2025-09-26 14:00 | flat_start_nr | 150.07 | 5 | 528 | 2025-09
2025-09-26 15:00 | flat_start_nr | 149.23 | 5 | 528 | 2025-09
2025-09-26 16:00 | flat_start_nr | 153.38 | 6 | 528 | 2025-09
2025-09-26 17:00 | flat_start_nr | 136.83 | 4 | 542 | 2025-09
2025-09-26 18:00 | flat_start_nr | 115.8 | 3 | 547 | 2025-09
2025-09-26 19:00 | flat_start_nr | 115.79 | 4 | 537 | 2025-09
2025-09-26 20:00 | flat_start_nr | 121.58 | 3 | 532 | 2025-09
2025-09-26 21:00 | flat_start_nr | 133.64 | 5 | 530 | 2025-09
2025-09-26 22:00 | flat_start_nr | 144.66 | 5 | 535 | 2025-09
2025-09-26 23:00 | flat_start_nr | 142.38 | 5 | 532 | 2025-09
2025-09-27 | flat_start_nr | 142.62 | 5 | 533 | 2025-09
2025-09-27 01:00 | flat_start_nr | 144.05 | 5 | 531 | 2025-09
2025-09-27 02:00 | flat_start_nr | 141.89 | 5 | 532 | 2025-09
2025-09-27 03:00 | flat_start_nr | 141.18 | 5 | 530 | 2025-09
2025-09-27 04:00 | flat_start_nr | 141.25 | 5 | 532 | 2025-09
2025-09-27 05:00 | flat_start_nr | 133.37 | 5 | 533 | 2025-09
2025-09-27 06:00 | flat_start_nr | 137.82 | 5 | 541 | 2025-09
2025-09-27 07:00 | flat_start_nr | 143.37 | 4 | 540 | 2025-09
2025-09-27 08:00 | flat_start_nr | 152.62 | 6 | 537 | 2025-09
2025-09-27 18:00 | flat_start_nr | 155.25 | 7 | 559 | 2025-09
2025-09-27 19:00 | flat_start_nr | 143.69 | 5 | 542 | 2025-09
2025-09-27 20:00 | flat_start_nr | 156.2 | 7 | 528 | 2025-09
2025-09-27 23:00 | flat_start_nr | 156.41 | 7 | 554 | 2025-09
2025-09-28 07:00 | flat_start_nr | 133.71 | 4 | 544 | 2025-09
2025-09-28 08:00 | flat_start_nr | 141.65 | 4 | 542 | 2025-09
2025-09-28 09:00 | flat_start_nr | 139.26 | 4 | 529 | 2025-09
2025-09-28 10:00 | flat_start_nr | 134.96 | 4 | 537 | 2025-09
2025-09-28 11:00 | flat_start_nr | 137.85 | 4 | 531 | 2025-09
2025-09-28 12:00 | flat_start_nr | 137.56 | 4 | 530 | 2025-09
2025-09-28 13:00 | flat_start_nr | 133.54 | 4 | 532 | 2025-09
2025-09-28 14:00 | flat_start_nr | 141.37 | 4 | 536 | 2025-09
2025-09-28 15:00 | flat_start_nr | 147.71 | 5 | 527 | 2025-09
2025-09-28 16:00 | flat_start_nr | 133.52 | 4 | 534 | 2025-09
2025-09-28 17:00 | flat_start_nr | 127.55 | 3 | 542 | 2025-09
2025-09-28 18:00 | flat_start_nr | 125.08 | 3 | 550 | 2025-09
2025-09-28 19:00 | flat_start_nr | 125.01 | 3 | 543 | 2025-09
2025-09-28 20:00 | flat_start_nr | 117.73 | 3 | 543 | 2025-09
2025-09-28 21:00 | flat_start_nr | 116.65 | 3 | 539 | 2025-09
2025-09-28 22:00 | flat_start_nr | 130.91 | 4 | 544 | 2025-09
2025-09-28 23:00 | flat_start_nr | 135.35 | 5 | 543 | 2025-09
2025-09-29 | flat_start_nr | 141.76 | 5 | 544 | 2025-09
2025-09-29 01:00 | flat_start_nr | 146.29 | 6 | 545 | 2025-09
2025-09-29 02:00 | flat_start_nr | 144.71 | 5 | 541 | 2025-09
2025-09-29 03:00 | flat_start_nr | 141.99 | 5 | 543 | 2025-09
2025-09-29 04:00 | flat_start_nr | 135.93 | 5 | 542 | 2025-09
2025-09-29 05:00 | flat_start_nr | 118.8 | 4 | 544 | 2025-09
2025-09-29 06:00 | flat_start_nr | 117.7 | 3 | 529 | 2025-09
2025-09-29 07:00 | flat_start_nr | 125.8 | 3 | 530 | 2025-09
2025-09-29 08:00 | flat_start_nr | 131.87 | 4 | 546 | 2025-09
2025-09-29 09:00 | flat_start_nr | 130.26 | 5 | 553 | 2025-09
2025-09-29 10:00 | flat_start_nr | 130.68 | 4 | 549 | 2025-09
2025-09-29 11:00 | flat_start_nr | 131.84 | 5 | 549 | 2025-09
2025-09-29 12:00 | flat_start_nr | 126.3 | 3 | 547 | 2025-09
2025-09-29 13:00 | flat_start_nr | 116.69 | 3 | 544 | 2025-09
2025-09-29 14:00 | flat_start_nr | 116.2 | 2 | 537 | 2025-09
2025-09-29 15:00 | flat_start_nr | 116.28 | 2 | 539 | 2025-09
2025-09-29 16:00 | flat_start_nr | 128.76 | 3 | 537 | 2025-09
2025-09-29 17:00 | flat_start_nr | 141.24 | 4 | 537 | 2025-09
2025-09-29 18:00 | flat_start_nr | 125.09 | 3 | 540 | 2025-09
2025-09-29 19:00 | flat_start_nr | 117.92 | 3 | 540 | 2025-09
2025-09-29 20:00 | flat_start_nr | 118.97 | 4 | 540 | 2025-09
2025-09-29 21:00 | flat_start_nr | 134.52 | 4 | 544 | 2025-09
2025-09-29 22:00 | flat_start_nr | 140.78 | 4 | 541 | 2025-09
2025-09-29 23:00 | flat_start_nr | 141.35 | 4 | 541 | 2025-09
2025-09-30 | flat_start_nr | 137.24 | 4 | 542 | 2025-09
2025-09-30 01:00 | flat_start_nr | 128.07 | 3 | 541 | 2025-09
2025-09-30 02:00 | flat_start_nr | 127.57 | 3 | 543 | 2025-09
2025-09-30 03:00 | flat_start_nr | 126.63 | 3 | 543 | 2025-09
2025-09-30 04:00 | flat_start_nr | 128.41 | 3 | 543 | 2025-09
2025-09-30 05:00 | flat_start_nr | 128.57 | 3 | 538 | 2025-09
2025-09-30 06:00 | flat_start_nr | 120.23 | 3 | 536 | 2025-09
2025-09-30 07:00 | flat_start_nr | 129.38 | 4 | 521 | 2025-09
2025-09-30 08:00 | flat_start_nr | 127.24 | 3 | 534 | 2025-09
2025-09-30 09:00 | flat_start_nr | 129.93 | 4 | 536 | 2025-09
2025-09-30 10:00 | flat_start_nr | 135.13 | 4 | 534 | 2025-09
2025-09-30 11:00 | flat_start_nr | 139.05 | 4 | 536 | 2025-09
2025-09-30 12:00 | flat_start_nr | 151.17 | 6 | 516 | 2025-09
2025-09-30 16:00 | flat_start_nr | 153.19 | 6 | 513 | 2025-09
2025-09-30 17:00 | flat_start_nr | 144.93 | 4 | 509 | 2025-09
2025-09-30 18:00 | flat_start_nr | 126.98 | 4 | 525 | 2025-09
2025-09-30 19:00 | flat_start_nr | 128.56 | 4 | 521 | 2025-09
2025-09-30 20:00 | flat_start_nr | 129.09 | 3 | 541 | 2025-09
2025-09-30 21:00 | flat_start_nr | 126.2 | 3 | 542 | 2025-09
2025-09-30 22:00 | flat_start_nr | 130.12 | 5 | 536 | 2025-09
2025-09-30 23:00 | flat_start_nr | 139.92 | 5 | 529 | 2025-09
2025-10-01 | flat_start_nr | 140.73 | 5 | 528 | 2025-10
2025-10-01 01:00 | flat_start_nr | 140.36 | 5 | 533 | 2025-10
2025-10-01 02:00 | flat_start_nr | 138.52 | 5 | 529 | 2025-10
2025-10-01 03:00 | flat_start_nr | 139.38 | 5 | 528 | 2025-10
2025-10-01 04:00 | flat_start_nr | 132.04 | 5 | 531 | 2025-10
2025-10-01 05:00 | flat_start_nr | 124.88 | 4 | 533 | 2025-10
2025-10-01 06:00 | flat_start_nr | 133.57 | 4 | 520 | 2025-10
2025-10-01 07:00 | flat_start_nr | 136.44 | 4 | 534 | 2025-10
2025-10-01 08:00 | flat_start_nr | 140.52 | 4 | 532 | 2025-10
2025-10-01 09:00 | flat_start_nr | 136.01 | 5 | 537 | 2025-10
2025-10-01 10:00 | flat_start_nr | 128.06 | 4 | 533 | 2025-10
2025-10-01 11:00 | flat_start_nr | 131.06 | 5 | 527 | 2025-10
2025-10-01 12:00 | flat_start_nr | 131.49 | 5 | 526 | 2025-10
2025-10-01 13:00 | flat_start_nr | 136.22 | 5 | 530 | 2025-10
2025-10-01 14:00 | flat_start_nr | 136.62 | 5 | 533 | 2025-10
2025-10-01 15:00 | flat_start_nr | 125.97 | 4 | 534 | 2025-10
2025-10-01 16:00 | flat_start_nr | 129.76 | 4 | 530 | 2025-10
2025-10-01 17:00 | flat_start_nr | 126.19 | 3 | 537 | 2025-10
2025-10-01 18:00 | flat_start_nr | 116.9 | 3 | 548 | 2025-10
2025-10-01 19:00 | flat_start_nr | 117.86 | 3 | 544 | 2025-10
2025-10-01 20:00 | flat_start_nr | 121.17 | 4 | 533 | 2025-10
2025-10-01 21:00 | flat_start_nr | 124.64 | 4 | 538 | 2025-10
2025-10-01 22:00 | flat_start_nr | 126.64 | 3 | 534 | 2025-10
2025-10-01 23:00 | flat_start_nr | 119.55 | 4 | 534 | 2025-10
2025-10-02 | flat_start_nr | 122.13 | 4 | 534 | 2025-10
2025-10-02 01:00 | flat_start_nr | 128.66 | 3 | 536 | 2025-10
2025-10-02 02:00 | flat_start_nr | 127.8 | 3 | 533 | 2025-10
2025-10-02 03:00 | flat_start_nr | 122.16 | 3 | 534 | 2025-10
2025-10-02 04:00 | flat_start_nr | 118.11 | 3 | 535 | 2025-10
2025-10-02 05:00 | flat_start_nr | 116.42 | 3 | 534 | 2025-10
2025-10-02 06:00 | flat_start_nr | 115.98 | 3 | 530 | 2025-10
2025-10-02 07:00 | flat_start_nr | 121.4 | 4 | 538 | 2025-10
2025-10-02 08:00 | flat_start_nr | 129.7 | 5 | 539 | 2025-10
2025-10-02 09:00 | flat_start_nr | 132.45 | 4 | 538 | 2025-10
2025-10-02 10:00 | flat_start_nr | 129.77 | 5 | 528 | 2025-10
2025-10-02 11:00 | flat_start_nr | 116 | 3 | 534 | 2025-10
2025-10-02 12:00 | flat_start_nr | 115.84 | 3 | 531 | 2025-10
2025-10-02 13:00 | flat_start_nr | 126.14 | 4 | 538 | 2025-10
2025-10-02 14:00 | flat_start_nr | 128.4 | 3 | 535 | 2025-10
2025-10-02 15:00 | flat_start_nr | 133.96 | 4 | 535 | 2025-10
2025-10-02 16:00 | flat_start_nr | 147.28 | 5 | 515 | 2025-10
2025-10-02 17:00 | flat_start_nr | 137.39 | 5 | 539 | 2025-10
2025-10-02 18:00 | flat_start_nr | 122.69 | 3 | 546 | 2025-10
2025-10-02 19:00 | flat_start_nr | 121.25 | 3 | 535 | 2025-10
2025-10-02 20:00 | flat_start_nr | 135.37 | 4 | 533 | 2025-10
2025-10-02 21:00 | flat_start_nr | 123.8 | 4 | 539 | 2025-10
2025-10-02 22:00 | flat_start_nr | 116.8 | 2 | 545 | 2025-10
2025-10-02 23:00 | flat_start_nr | 120.21 | 3 | 550 | 2025-10
2025-10-03 | flat_start_nr | 127.06 | 3 | 548 | 2025-10
2025-10-03 01:00 | flat_start_nr | 135.17 | 4 | 541 | 2025-10
2025-10-03 02:00 | flat_start_nr | 133.67 | 4 | 537 | 2025-10
2025-10-03 03:00 | flat_start_nr | 131.59 | 4 | 537 | 2025-10
2025-10-03 04:00 | flat_start_nr | 128.8 | 4 | 534 | 2025-10
2025-10-03 05:00 | flat_start_nr | 115.38 | 3 | 539 | 2025-10
2025-10-03 06:00 | flat_start_nr | 112.14 | 3 | 545 | 2025-10
2025-10-03 07:00 | flat_start_nr | 119.98 | 4 | 539 | 2025-10
2025-10-03 08:00 | flat_start_nr | 119.07 | 4 | 544 | 2025-10
2025-10-03 09:00 | flat_start_nr | 122.16 | 4 | 540 | 2025-10
2025-10-03 10:00 | flat_start_nr | 127.12 | 4 | 540 | 2025-10
2025-10-03 11:00 | flat_start_nr | 127.64 | 4 | 538 | 2025-10
2025-10-03 12:00 | flat_start_nr | 134.12 | 4 | 534 | 2025-10
2025-10-03 13:00 | flat_start_nr | 139.16 | 4 | 528 | 2025-10
2025-10-03 14:00 | flat_start_nr | 141.42 | 4 | 535 | 2025-10
2025-10-03 15:00 | flat_start_nr | 144.02 | 4 | 527 | 2025-10
2025-10-03 16:00 | flat_start_nr | 148.39 | 5 | 527 | 2025-10
2025-10-03 17:00 | flat_start_nr | 139.91 | 3 | 550 | 2025-10
2025-10-03 18:00 | flat_start_nr | 123.01 | 2 | 556 | 2025-10
2025-10-03 19:00 | flat_start_nr | 112.02 | 2 | 555 | 2025-10
2025-10-03 20:00 | flat_start_nr | 128.71 | 3 | 543 | 2025-10
2025-10-03 21:00 | flat_start_nr | 115.09 | 2 | 551 | 2025-10
2025-10-03 22:00 | flat_start_nr | 127.51 | 3 | 548 | 2025-10
2025-10-03 23:00 | flat_start_nr | 128.82 | 3 | 543 | 2025-10
2025-10-04 | flat_start_nr | 109.67 | 2 | 541 | 2025-10
2025-10-04 01:00 | flat_start_nr | 110.03 | 2 | 547 | 2025-10
2025-10-04 02:00 | flat_start_nr | 111.47 | 2 | 544 | 2025-10
2025-10-04 03:00 | flat_start_nr | 125.47 | 3 | 546 | 2025-10
2025-10-04 04:00 | flat_start_nr | 122.22 | 3 | 541 | 2025-10
2025-10-04 05:00 | flat_start_nr | 127.25 | 3 | 546 | 2025-10
2025-10-04 06:00 | flat_start_nr | 133.79 | 4 | 547 | 2025-10
2025-10-04 07:00 | flat_start_nr | 138.76 | 4 | 550 | 2025-10
2025-10-04 08:00 | flat_start_nr | 122.4 | 3 | 546 | 2025-10
2025-10-04 09:00 | flat_start_nr | 117.85 | 4 | 548 | 2025-10
2025-10-04 10:00 | flat_start_nr | 116.82 | 4 | 551 | 2025-10
2025-10-04 11:00 | flat_start_nr | 120.86 | 4 | 544 | 2025-10
2025-10-04 12:00 | flat_start_nr | 121.79 | 4 | 543 | 2025-10
2025-10-04 13:00 | flat_start_nr | 124.22 | 3 | 537 | 2025-10
2025-10-04 14:00 | flat_start_nr | 119.59 | 4 | 548 | 2025-10
2025-10-04 15:00 | flat_start_nr | 115.91 | 4 | 545 | 2025-10
2025-10-04 16:00 | flat_start_nr | 116.51 | 4 | 531 | 2025-10
2025-10-04 17:00 | flat_start_nr | 115.3 | 3 | 535 | 2025-10
2025-10-04 18:00 | flat_start_nr | 115.05 | 2 | 549 | 2025-10
2025-10-04 19:00 | flat_start_nr | 113.32 | 2 | 548 | 2025-10
2025-10-04 20:00 | flat_start_nr | 116.03 | 3 | 549 | 2025-10
2025-10-04 21:00 | flat_start_nr | 121.96 | 4 | 555 | 2025-10
2025-10-04 22:00 | flat_start_nr | 139.23 | 5 | 562 | 2025-10
2025-10-04 23:00 | flat_start_nr | 148.69 | 6 | 556 | 2025-10
2025-10-05 01:00 | flat_start_nr | 158.57 | 6 | 551 | 2025-10
2025-10-05 02:00 | flat_start_nr | 148.85 | 5 | 552 | 2025-10
2025-10-05 03:00 | flat_start_nr | 135.14 | 5 | 560 | 2025-10
2025-10-05 04:00 | flat_start_nr | 128.18 | 4 | 556 | 2025-10
2025-10-05 05:00 | flat_start_nr | 137.63 | 4 | 565 | 2025-10
2025-10-05 06:00 | flat_start_nr | 141.25 | 4 | 548 | 2025-10
2025-10-05 07:00 | flat_start_nr | 140.07 | 4 | 563 | 2025-10
2025-10-05 08:00 | flat_start_nr | 134.74 | 4 | 559 | 2025-10
2025-10-05 09:00 | flat_start_nr | 139.29 | 4 | 546 | 2025-10
2025-10-05 10:00 | flat_start_nr | 153.52 | 6 | 542 | 2025-10
2025-10-05 11:00 | flat_start_nr | 153.21 | 6 | 525 | 2025-10
2025-10-05 18:00 | flat_start_nr | 143.91 | 3 | 581 | 2025-10
2025-10-05 19:00 | flat_start_nr | 151.05 | 4 | 564 | 2025-10
2025-10-05 20:00 | flat_start_nr | 156.08 | 5 | 568 | 2025-10
2025-10-05 21:00 | flat_start_nr | 153.68 | 6 | 532 | 2025-10
2025-10-05 22:00 | flat_start_nr | 144.24 | 5 | 557 | 2025-10
2025-10-05 23:00 | flat_start_nr | 140.72 | 6 | 556 | 2025-10
2025-10-06 | flat_start_nr | 142.17 | 5 | 556 | 2025-10
2025-10-06 01:00 | flat_start_nr | 145.94 | 6 | 543 | 2025-10
2025-10-06 02:00 | flat_start_nr | 146.04 | 5 | 550 | 2025-10
2025-10-06 03:00 | flat_start_nr | 141.57 | 4 | 559 | 2025-10
2025-10-06 04:00 | flat_start_nr | 135.88 | 4 | 554 | 2025-10
2025-10-06 05:00 | flat_start_nr | 135.02 | 4 | 560 | 2025-10
2025-10-06 06:00 | flat_start_nr | 141.48 | 4 | 558 | 2025-10
2025-10-06 07:00 | flat_start_nr | 147.29 | 5 | 548 | 2025-10
2025-10-06 08:00 | flat_start_nr | 149.44 | 5 | 533 | 2025-10
2025-10-06 09:00 | flat_start_nr | 145.44 | 4 | 544 | 2025-10
2025-10-06 10:00 | flat_start_nr | 143.68 | 4 | 553 | 2025-10
2025-10-06 11:00 | flat_start_nr | 145.48 | 5 | 542 | 2025-10
2025-10-06 12:00 | flat_start_nr | 143.94 | 4 | 556 | 2025-10
2025-10-06 13:00 | flat_start_nr | 140.35 | 4 | 553 | 2025-10
2025-10-06 14:00 | flat_start_nr | 137.51 | 4 | 555 | 2025-10
2025-10-06 15:00 | flat_start_nr | 144.06 | 4 | 571 | 2025-10
2025-10-06 17:00 | flat_start_nr | 143.27 | 4 | 552 | 2025-10
2025-10-06 18:00 | flat_start_nr | 125.08 | 3 | 552 | 2025-10
2025-10-06 19:00 | flat_start_nr | 137.69 | 3 | 566 | 2025-10
2025-10-06 20:00 | flat_start_nr | 152.3 | 5 | 544 | 2025-10
2025-10-06 22:00 | flat_start_nr | 142.16 | 4 | 557 | 2025-10
2025-10-07 | flat_start_nr | 157.55 | 6 | 547 | 2025-10
2025-10-07 04:00 | flat_start_nr | 145.49 | 5 | 547 | 2025-10
2025-10-07 05:00 | flat_start_nr | 136 | 4 | 544 | 2025-10
2025-10-07 06:00 | flat_start_nr | 132.94 | 4 | 555 | 2025-10
2025-10-07 07:00 | flat_start_nr | 136.48 | 4 | 553 | 2025-10
2025-10-07 08:00 | flat_start_nr | 145.96 | 5 | 534 | 2025-10
2025-10-07 09:00 | flat_start_nr | 145.44 | 5 | 531 | 2025-10
2025-10-07 10:00 | flat_start_nr | 145.01 | 4 | 531 | 2025-10
2025-10-07 11:00 | flat_start_nr | 149.08 | 5 | 526 | 2025-10
2025-10-07 12:00 | flat_start_nr | 156.07 | 6 | 532 | 2025-10
2025-10-07 18:00 | flat_start_nr | 135.59 | 5 | 543 | 2025-10
2025-10-07 19:00 | flat_start_nr | 134.03 | 5 | 545 | 2025-10
2025-10-07 20:00 | flat_start_nr | 137.27 | 5 | 541 | 2025-10
2025-10-07 21:00 | flat_start_nr | 145.36 | 6 | 545 | 2025-10
2025-10-07 22:00 | flat_start_nr | 157.52 | 7 | 548 | 2025-10
2025-10-07 23:00 | flat_start_nr | 158.98 | 7 | 536 | 2025-10
2025-10-08 | normal_nr | 160.81 | 7 | 557 | 2025-10
2025-10-08 05:00 | flat_start_nr | 152.45 | 6 | 536 | 2025-10
2025-10-08 06:00 | flat_start_nr | 142.24 | 6 | 551 | 2025-10
2025-10-08 10:00 | flat_start_nr | 145.75 | 5 | 530 | 2025-10
2025-10-08 11:00 | flat_start_nr | 137.76 | 4 | 545 | 2025-10
2025-10-08 12:00 | flat_start_nr | 133.96 | 4 | 544 | 2025-10
2025-10-08 13:00 | flat_start_nr | 147.36 | 5 | 530 | 2025-10
2025-10-08 14:00 | flat_start_nr | 147.6 | 5 | 529 | 2025-10
2025-10-08 18:00 | flat_start_nr | 140.03 | 3 | 578 | 2025-10
2025-10-08 19:00 | flat_start_nr | 144.92 | 3 | 573 | 2025-10
2025-10-08 20:00 | flat_start_nr | 141.73 | 3 | 576 | 2025-10
2025-10-08 21:00 | flat_start_nr | 144.93 | 4 | 552 | 2025-10
2025-10-08 22:00 | flat_start_nr | 139.88 | 4 | 545 | 2025-10
2025-10-08 23:00 | flat_start_nr | 128.47 | 3 | 550 | 2025-10
2025-10-09 | flat_start_nr | 137.76 | 4 | 541 | 2025-10
2025-10-09 01:00 | flat_start_nr | 139.83 | 4 | 541 | 2025-10
2025-10-09 02:00 | flat_start_nr | 143.46 | 4 | 541 | 2025-10
2025-10-09 03:00 | flat_start_nr | 136.04 | 4 | 547 | 2025-10
2025-10-09 04:00 | flat_start_nr | 139.52 | 4 | 548 | 2025-10
2025-10-09 05:00 | flat_start_nr | 143.28 | 4 | 564 | 2025-10
2025-10-09 06:00 | flat_start_nr | 143.92 | 3 | 579 | 2025-10
2025-10-09 07:00 | flat_start_nr | 149.31 | 4 | 547 | 2025-10
2025-10-09 09:00 | flat_start_nr | 150.94 | 6 | 531 | 2025-10
2025-10-09 10:00 | flat_start_nr | 136.63 | 4 | 535 | 2025-10
2025-10-09 11:00 | flat_start_nr | 130.23 | 4 | 528 | 2025-10
2025-10-09 12:00 | flat_start_nr | 129.37 | 4 | 524 | 2025-10
2025-10-09 13:00 | flat_start_nr | 133.22 | 5 | 528 | 2025-10
2025-10-09 14:00 | flat_start_nr | 132.9 | 5 | 530 | 2025-10
2025-10-09 15:00 | flat_start_nr | 127.91 | 3 | 536 | 2025-10
2025-10-09 16:00 | flat_start_nr | 120.76 | 4 | 537 | 2025-10
2025-10-09 17:00 | flat_start_nr | 117.5 | 4 | 536 | 2025-10
2025-10-09 18:00 | flat_start_nr | 112.94 | 2 | 542 | 2025-10
2025-10-09 19:00 | flat_start_nr | 116.4 | 3 | 545 | 2025-10
2025-10-09 20:00 | flat_start_nr | 116.52 | 3 | 548 | 2025-10
2025-10-09 21:00 | flat_start_nr | 116.54 | 3 | 547 | 2025-10
2025-10-09 22:00 | flat_start_nr | 118.1 | 3 | 538 | 2025-10
2025-10-09 23:00 | flat_start_nr | 124.31 | 3 | 537 | 2025-10
2025-10-10 | flat_start_nr | 124.61 | 4 | 531 | 2025-10
2025-10-10 01:00 | flat_start_nr | 121.51 | 4 | 536 | 2025-10
2025-10-10 02:00 | flat_start_nr | 122.03 | 4 | 537 | 2025-10
2025-10-10 03:00 | flat_start_nr | 117.07 | 5 | 539 | 2025-10
2025-10-10 04:00 | flat_start_nr | 116.51 | 3 | 537 | 2025-10
2025-10-10 05:00 | flat_start_nr | 116.2 | 2 | 542 | 2025-10
2025-10-10 06:00 | flat_start_nr | 116.14 | 2 | 551 | 2025-10
2025-10-10 07:00 | flat_start_nr | 115.73 | 3 | 542 | 2025-10
2025-10-10 08:00 | flat_start_nr | 127.08 | 3 | 542 | 2025-10
2025-10-10 09:00 | flat_start_nr | 124.38 | 3 | 541 | 2025-10
2025-10-10 10:00 | flat_start_nr | 130.62 | 4 | 541 | 2025-10
2025-10-10 11:00 | flat_start_nr | 127.62 | 3 | 534 | 2025-10
2025-10-10 12:00 | flat_start_nr | 133.78 | 4 | 536 | 2025-10
2025-10-10 13:00 | flat_start_nr | 136.56 | 4 | 534 | 2025-10
2025-10-10 14:00 | flat_start_nr | 135.12 | 5 | 535 | 2025-10
2025-10-10 15:00 | flat_start_nr | 127.55 | 3 | 537 | 2025-10
2025-10-10 16:00 | flat_start_nr | 116.39 | 2 | 540 | 2025-10
2025-10-10 17:00 | flat_start_nr | 114.11 | 2 | 537 | 2025-10
2025-10-10 18:00 | flat_start_nr | 116.67 | 2 | 544 | 2025-10
2025-10-10 19:00 | flat_start_nr | 117.62 | 4 | 540 | 2025-10
2025-10-10 20:00 | flat_start_nr | 117.67 | 3 | 538 | 2025-10
2025-10-10 21:00 | flat_start_nr | 117.43 | 3 | 538 | 2025-10
2025-10-10 22:00 | flat_start_nr | 137.49 | 4 | 544 | 2025-10
2025-10-11 | flat_start_nr | 157.14 | 5 | 563 | 2025-10
2025-10-11 03:00 | flat_start_nr | 157.64 | 5 | 547 | 2025-10
2025-10-11 05:00 | normal_nr | 159.26 | 5 | 555 | 2025-10
2025-10-11 17:00 | flat_start_nr | 148.62 | 4 | 532 | 2025-10
2025-10-11 18:00 | flat_start_nr | 127.15 | 4 | 547 | 2025-10
2025-10-11 19:00 | flat_start_nr | 128.7 | 4 | 549 | 2025-10
2025-10-11 20:00 | flat_start_nr | 128.85 | 4 | 550 | 2025-10
2025-10-11 21:00 | flat_start_nr | 129.36 | 4 | 550 | 2025-10
2025-10-11 22:00 | flat_start_nr | 138.85 | 4 | 544 | 2025-10
2025-10-11 23:00 | flat_start_nr | 149.18 | 5 | 534 | 2025-10
2025-10-12 | flat_start_nr | 143.71 | 4 | 549 | 2025-10
2025-10-12 01:00 | flat_start_nr | 148.27 | 5 | 544 | 2025-10
2025-10-12 02:00 | flat_start_nr | 143.9 | 4 | 557 | 2025-10
2025-10-12 03:00 | flat_start_nr | 140.38 | 5 | 563 | 2025-10
2025-10-12 04:00 | flat_start_nr | 136.72 | 5 | 559 | 2025-10
2025-10-12 05:00 | flat_start_nr | 134.04 | 5 | 552 | 2025-10
2025-10-12 06:00 | flat_start_nr | 127.5 | 4 | 545 | 2025-10
2025-10-12 07:00 | flat_start_nr | 133.15 | 5 | 545 | 2025-10
2025-10-12 08:00 | flat_start_nr | 138.17 | 3 | 538 | 2025-10
2025-10-12 09:00 | flat_start_nr | 132.69 | 4 | 549 | 2025-10
2025-10-12 10:00 | flat_start_nr | 128.38 | 3 | 540 | 2025-10
2025-10-12 11:00 | flat_start_nr | 130.71 | 4 | 542 | 2025-10
2025-10-12 12:00 | flat_start_nr | 138.9 | 3 | 539 | 2025-10
2025-10-12 13:00 | flat_start_nr | 149.82 | 4 | 530 | 2025-10
2025-10-12 14:00 | flat_start_nr | 153.94 | 5 | 527 | 2025-10
2025-10-12 17:00 | flat_start_nr | 144.86 | 3 | 553 | 2025-10
2025-10-12 18:00 | flat_start_nr | 130.52 | 4 | 540 | 2025-10
2025-10-12 19:00 | flat_start_nr | 132.05 | 4 | 544 | 2025-10
2025-10-12 20:00 | flat_start_nr | 130.84 | 4 | 545 | 2025-10
2025-10-12 21:00 | flat_start_nr | 125.54 | 3 | 545 | 2025-10
2025-10-12 22:00 | flat_start_nr | 129.51 | 4 | 544 | 2025-10
2025-10-12 23:00 | flat_start_nr | 136.26 | 4 | 546 | 2025-10
2025-10-13 | flat_start_nr | 142.62 | 4 | 564 | 2025-10
2025-10-13 01:00 | flat_start_nr | 137.65 | 4 | 551 | 2025-10
2025-10-13 02:00 | flat_start_nr | 125.22 | 3 | 545 | 2025-10
2025-10-13 03:00 | flat_start_nr | 125.78 | 3 | 534 | 2025-10
2025-10-13 04:00 | flat_start_nr | 127.58 | 3 | 525 | 2025-10
2025-10-13 05:00 | flat_start_nr | 131.69 | 4 | 525 | 2025-10
2025-10-13 06:00 | flat_start_nr | 124.43 | 3 | 545 | 2025-10
2025-10-13 07:00 | flat_start_nr | 127.15 | 3 | 534 | 2025-10
2025-10-13 08:00 | flat_start_nr | 129.17 | 4 | 530 | 2025-10
2025-10-13 09:00 | flat_start_nr | 138.88 | 4 | 532 | 2025-10
2025-10-13 10:00 | flat_start_nr | 137.8 | 4 | 525 | 2025-10
2025-10-13 11:00 | flat_start_nr | 138.32 | 4 | 530 | 2025-10
2025-10-13 12:00 | flat_start_nr | 134.77 | 4 | 522 | 2025-10
2025-10-13 13:00 | flat_start_nr | 131.66 | 4 | 521 | 2025-10
2025-10-13 14:00 | flat_start_nr | 129.67 | 4 | 536 | 2025-10
2025-10-13 15:00 | flat_start_nr | 137.63 | 3 | 552 | 2025-10
2025-10-13 16:00 | flat_start_nr | 135.97 | 3 | 553 | 2025-10
2025-10-13 17:00 | flat_start_nr | 137.44 | 3 | 554 | 2025-10
2025-10-13 18:00 | flat_start_nr | 122.21 | 2 | 550 | 2025-10
2025-10-13 19:00 | flat_start_nr | 133.5 | 3 | 543 | 2025-10
2025-10-13 20:00 | flat_start_nr | 123.14 | 3 | 537 | 2025-10
2025-10-13 21:00 | flat_start_nr | 115.91 | 3 | 542 | 2025-10
2025-10-13 22:00 | flat_start_nr | 126.89 | 4 | 536 | 2025-10
2025-10-13 23:00 | flat_start_nr | 130.95 | 4 | 547 | 2025-10
2025-10-14 | flat_start_nr | 120.19 | 3 | 539 | 2025-10
2025-10-14 01:00 | flat_start_nr | 115.97 | 3 | 545 | 2025-10
2025-10-14 02:00 | flat_start_nr | 115.81 | 3 | 549 | 2025-10
2025-10-14 03:00 | flat_start_nr | 115.71 | 3 | 551 | 2025-10
2025-10-14 04:00 | flat_start_nr | 115.47 | 2 | 548 | 2025-10
2025-10-14 05:00 | flat_start_nr | 115.52 | 2 | 550 | 2025-10
2025-10-14 06:00 | flat_start_nr | 115.4 | 2 | 548 | 2025-10
2025-10-14 07:00 | flat_start_nr | 115.44 | 3 | 544 | 2025-10
2025-10-14 08:00 | flat_start_nr | 119.1 | 4 | 545 | 2025-10
2025-10-14 09:00 | flat_start_nr | 116.25 | 4 | 544 | 2025-10
2025-10-14 10:00 | flat_start_nr | 114.23 | 3 | 539 | 2025-10
2025-10-14 11:00 | flat_start_nr | 116.72 | 4 | 536 | 2025-10
2025-10-14 12:00 | flat_start_nr | 116.39 | 4 | 532 | 2025-10
2025-10-14 13:00 | flat_start_nr | 116.45 | 3 | 537 | 2025-10
2025-10-14 14:00 | flat_start_nr | 116.61 | 3 | 535 | 2025-10
2025-10-14 15:00 | flat_start_nr | 116.34 | 3 | 537 | 2025-10
2025-10-14 16:00 | flat_start_nr | 116.24 | 3 | 540 | 2025-10
2025-10-14 17:00 | flat_start_nr | 115.64 | 4 | 539 | 2025-10
2025-10-14 18:00 | flat_start_nr | 113.53 | 2 | 544 | 2025-10
2025-10-14 19:00 | flat_start_nr | 113.98 | 2 | 545 | 2025-10
2025-10-14 20:00 | flat_start_nr | 115.84 | 2 | 544 | 2025-10
2025-10-14 21:00 | flat_start_nr | 115.92 | 3 | 541 | 2025-10
2025-10-14 22:00 | flat_start_nr | 115.69 | 3 | 550 | 2025-10
2025-10-14 23:00 | flat_start_nr | 115.72 | 2 | 548 | 2025-10
2025-10-15 | flat_start_nr | 115.94 | 3 | 548 | 2025-10
2025-10-15 01:00 | flat_start_nr | 115.89 | 3 | 547 | 2025-10
2025-10-15 02:00 | flat_start_nr | 115.91 | 3 | 550 | 2025-10
2025-10-15 03:00 | flat_start_nr | 115.99 | 3 | 547 | 2025-10
2025-10-15 04:00 | flat_start_nr | 115.93 | 3 | 548 | 2025-10
2025-10-15 05:00 | flat_start_nr | 116.2 | 3 | 547 | 2025-10
2025-10-15 06:00 | flat_start_nr | 116.27 | 3 | 544 | 2025-10
2025-10-15 07:00 | flat_start_nr | 122.03 | 3 | 539 | 2025-10
2025-10-15 08:00 | flat_start_nr | 136.16 | 4 | 538 | 2025-10
2025-10-15 09:00 | flat_start_nr | 142.05 | 4 | 540 | 2025-10
2025-10-15 10:00 | flat_start_nr | 140.89 | 4 | 544 | 2025-10
2025-10-15 11:00 | flat_start_nr | 140.77 | 4 | 542 | 2025-10
2025-10-15 12:00 | flat_start_nr | 134.45 | 4 | 536 | 2025-10
2025-10-15 13:00 | flat_start_nr | 128.88 | 3 | 535 | 2025-10
2025-10-15 14:00 | flat_start_nr | 119.61 | 3 | 538 | 2025-10
2025-10-15 15:00 | flat_start_nr | 130.96 | 4 | 537 | 2025-10
2025-10-15 16:00 | flat_start_nr | 131.67 | 3 | 545 | 2025-10
2025-10-15 17:00 | flat_start_nr | 133.45 | 3 | 540 | 2025-10
2025-10-15 18:00 | flat_start_nr | 113.36 | 2 | 547 | 2025-10
2025-10-15 19:00 | flat_start_nr | 117.2 | 2 | 548 | 2025-10
2025-10-15 20:00 | flat_start_nr | 112.1 | 3 | 539 | 2025-10
2025-10-15 21:00 | flat_start_nr | 116.54 | 4 | 541 | 2025-10
2025-10-15 22:00 | flat_start_nr | 116.27 | 3 | 543 | 2025-10
2025-10-15 23:00 | flat_start_nr | 115.96 | 3 | 545 | 2025-10
2025-10-16 | flat_start_nr | 116.02 | 3 | 547 | 2025-10
2025-10-16 01:00 | flat_start_nr | 125.19 | 4 | 546 | 2025-10
2025-10-16 02:00 | flat_start_nr | 132.93 | 5 | 537 | 2025-10
2025-10-16 03:00 | flat_start_nr | 128.19 | 4 | 537 | 2025-10
2025-10-16 04:00 | flat_start_nr | 116.25 | 3 | 541 | 2025-10
2025-10-16 05:00 | flat_start_nr | 115.69 | 3 | 541 | 2025-10
2025-10-16 06:00 | flat_start_nr | 126.34 | 3 | 544 | 2025-10
2025-10-16 07:00 | flat_start_nr | 139.01 | 4 | 545 | 2025-10
2025-10-16 08:00 | flat_start_nr | 139.63 | 4 | 550 | 2025-10
2025-10-16 09:00 | flat_start_nr | 141.42 | 4 | 535 | 2025-10
2025-10-16 10:00 | flat_start_nr | 145.87 | 5 | 508 | 2025-10
2025-10-16 11:00 | flat_start_nr | 129.72 | 4 | 533 | 2025-10
2025-10-16 12:00 | flat_start_nr | 122.88 | 3 | 531 | 2025-10
2025-10-16 13:00 | flat_start_nr | 134.01 | 4 | 534 | 2025-10
2025-10-16 14:00 | flat_start_nr | 145.31 | 4 | 523 | 2025-10
2025-10-16 15:00 | flat_start_nr | 154.47 | 6 | 529 | 2025-10
2025-10-16 16:00 | flat_start_nr | 148.7 | 5 | 515 | 2025-10
2025-10-16 17:00 | flat_start_nr | 151.31 | 6 | 537 | 2025-10
2025-10-16 18:00 | flat_start_nr | 131.14 | 4 | 533 | 2025-10
2025-10-16 19:00 | flat_start_nr | 129.31 | 4 | 536 | 2025-10
2025-10-16 20:00 | flat_start_nr | 130 | 5 | 543 | 2025-10
2025-10-16 21:00 | flat_start_nr | 132.43 | 5 | 536 | 2025-10
2025-10-16 22:00 | flat_start_nr | 137.55 | 5 | 535 | 2025-10
2025-10-16 23:00 | flat_start_nr | 146.79 | 6 | 536 | 2025-10
2025-10-17 | flat_start_nr | 156.33 | 7 | 521 | 2025-10
2025-10-17 03:00 | normal_nr | 161.13 | 6 | 552 | 2025-10
2025-10-17 04:00 | flat_start_nr | 152.67 | 7 | 530 | 2025-10
2025-10-17 05:00 | flat_start_nr | 141.42 | 5 | 550 | 2025-10
2025-10-17 06:00 | flat_start_nr | 123.94 | 3 | 543 | 2025-10
2025-10-17 07:00 | flat_start_nr | 134.19 | 4 | 543 | 2025-10
2025-10-17 08:00 | flat_start_nr | 142.03 | 4 | 549 | 2025-10
2025-10-17 09:00 | flat_start_nr | 147.96 | 5 | 520 | 2025-10
2025-10-17 10:00 | flat_start_nr | 149.63 | 6 | 522 | 2025-10
2025-10-17 11:00 | flat_start_nr | 149.37 | 6 | 522 | 2025-10
2025-10-17 12:00 | flat_start_nr | 138.09 | 4 | 540 | 2025-10
2025-10-17 13:00 | flat_start_nr | 134.28 | 4 | 539 | 2025-10
2025-10-17 14:00 | flat_start_nr | 127.7 | 3 | 543 | 2025-10
2025-10-17 15:00 | flat_start_nr | 130.91 | 4 | 554 | 2025-10
2025-10-17 16:00 | flat_start_nr | 138.04 | 4 | 552 | 2025-10
2025-10-17 17:00 | flat_start_nr | 139.88 | 4 | 547 | 2025-10
2025-10-17 18:00 | flat_start_nr | 116.26 | 2 | 543 | 2025-10
2025-10-17 19:00 | flat_start_nr | 120.97 | 3 | 541 | 2025-10
2025-10-17 20:00 | flat_start_nr | 120.04 | 3 | 547 | 2025-10
2025-10-17 21:00 | flat_start_nr | 125.6 | 3 | 533 | 2025-10
2025-10-17 22:00 | flat_start_nr | 134.99 | 4 | 529 | 2025-10
2025-10-17 23:00 | flat_start_nr | 141.22 | 4 | 530 | 2025-10
2025-10-18 | flat_start_nr | 157.67 | 5 | 552 | 2025-10
2025-10-18 01:00 | flat_start_nr | 156.82 | 5 | 557 | 2025-10
2025-10-18 02:00 | flat_start_nr | 151.9 | 5 | 534 | 2025-10
2025-10-18 03:00 | flat_start_nr | 148.47 | 5 | 537 | 2025-10
2025-10-18 04:00 | flat_start_nr | 147.35 | 5 | 537 | 2025-10
2025-10-18 05:00 | flat_start_nr | 141.09 | 4 | 541 | 2025-10
2025-10-18 06:00 | flat_start_nr | 148.87 | 4 | 531 | 2025-10
2025-10-18 07:00 | flat_start_nr | 155.68 | 5 | 539 | 2025-10
2025-10-18 13:00 | flat_start_nr | 155.12 | 6 | 545 | 2025-10
2025-10-18 17:00 | flat_start_nr | 148.32 | 5 | 531 | 2025-10
2025-10-18 18:00 | flat_start_nr | 138.96 | 4 | 539 | 2025-10
2025-10-18 19:00 | flat_start_nr | 142.34 | 5 | 544 | 2025-10
2025-10-18 20:00 | flat_start_nr | 142.18 | 5 | 544 | 2025-10
2025-10-18 21:00 | flat_start_nr | 142.7 | 5 | 547 | 2025-10
2025-10-18 22:00 | flat_start_nr | 147.33 | 6 | 543 | 2025-10
2025-10-18 23:00 | flat_start_nr | 148.29 | 6 | 537 | 2025-10
2025-10-19 | flat_start_nr | 153.92 | 7 | 528 | 2025-10
2025-10-19 01:00 | flat_start_nr | 155.81 | 7 | 530 | 2025-10
2025-10-19 02:00 | flat_start_nr | 159.08 | 7 | 548 | 2025-10
2025-10-19 03:00 | flat_start_nr | 159.62 | 6 | 541 | 2025-10
2025-10-19 04:00 | flat_start_nr | 153.31 | 7 | 533 | 2025-10
2025-10-19 05:00 | flat_start_nr | 145.05 | 4 | 553 | 2025-10
2025-10-19 06:00 | flat_start_nr | 139.42 | 5 | 546 | 2025-10
2025-10-19 07:00 | flat_start_nr | 142.34 | 5 | 543 | 2025-10
2025-10-19 08:00 | flat_start_nr | 139.79 | 5 | 538 | 2025-10
2025-10-19 09:00 | flat_start_nr | 142.17 | 5 | 538 | 2025-10
2025-10-19 10:00 | flat_start_nr | 144.47 | 4 | 534 | 2025-10
2025-10-19 11:00 | flat_start_nr | 150.23 | 5 | 530 | 2025-10
2025-10-19 14:00 | flat_start_nr | 151.41 | 5 | 520 | 2025-10
2025-10-19 15:00 | flat_start_nr | 131.01 | 4 | 529 | 2025-10
2025-10-19 16:00 | flat_start_nr | 128.58 | 3 | 539 | 2025-10
2025-10-19 17:00 | flat_start_nr | 124.22 | 3 | 541 | 2025-10
2025-10-19 18:00 | flat_start_nr | 116.91 | 2 | 542 | 2025-10
2025-10-19 19:00 | flat_start_nr | 121.56 | 3 | 545 | 2025-10
2025-10-19 20:00 | flat_start_nr | 134.04 | 4 | 546 | 2025-10
2025-10-19 21:00 | flat_start_nr | 137.04 | 5 | 550 | 2025-10
2025-10-19 22:00 | flat_start_nr | 139.03 | 4 | 549 | 2025-10
2025-10-19 23:00 | flat_start_nr | 147.27 | 6 | 551 | 2025-10
2025-10-20 | flat_start_nr | 141.27 | 5 | 560 | 2025-10
2025-10-20 01:00 | flat_start_nr | 138.39 | 5 | 538 | 2025-10
2025-10-20 02:00 | flat_start_nr | 137.49 | 5 | 541 | 2025-10
2025-10-20 03:00 | flat_start_nr | 140.01 | 5 | 552 | 2025-10
2025-10-20 04:00 | flat_start_nr | 136.17 | 5 | 544 | 2025-10
2025-10-20 05:00 | flat_start_nr | 129.52 | 4 | 539 | 2025-10
2025-10-20 06:00 | flat_start_nr | 138.29 | 6 | 542 | 2025-10
2025-10-20 07:00 | flat_start_nr | 152.65 | 6 | 532 | 2025-10
2025-10-20 08:00 | flat_start_nr | 146.65 | 5 | 529 | 2025-10
2025-10-20 09:00 | flat_start_nr | 147.04 | 5 | 533 | 2025-10
2025-10-20 10:00 | flat_start_nr | 144.45 | 4 | 536 | 2025-10
2025-10-20 11:00 | flat_start_nr | 138.7 | 4 | 527 | 2025-10
2025-10-20 12:00 | flat_start_nr | 135.33 | 4 | 535 | 2025-10
2025-10-20 13:00 | flat_start_nr | 137.6 | 4 | 538 | 2025-10
2025-10-20 14:00 | flat_start_nr | 144.23 | 4 | 531 | 2025-10
2025-10-20 15:00 | flat_start_nr | 147.29 | 5 | 521 | 2025-10
2025-10-20 16:00 | flat_start_nr | 148.74 | 6 | 527 | 2025-10
2025-10-20 17:00 | flat_start_nr | 120.49 | 4 | 537 | 2025-10
2025-10-20 18:00 | flat_start_nr | 128.83 | 3 | 553 | 2025-10
2025-10-20 19:00 | flat_start_nr | 130.68 | 4 | 534 | 2025-10
2025-10-20 20:00 | flat_start_nr | 133.48 | 4 | 535 | 2025-10
2025-10-20 21:00 | flat_start_nr | 131.58 | 4 | 537 | 2025-10
2025-10-20 22:00 | flat_start_nr | 146.81 | 5 | 541 | 2025-10
2025-10-20 23:00 | flat_start_nr | 151.01 | 4 | 533 | 2025-10
2025-10-21 | flat_start_nr | 153.93 | 5 | 528 | 2025-10
2025-10-21 01:00 | flat_start_nr | 153.22 | 5 | 529 | 2025-10
2025-10-21 02:00 | flat_start_nr | 152.94 | 5 | 529 | 2025-10
2025-10-21 03:00 | flat_start_nr | 140.57 | 4 | 541 | 2025-10
2025-10-21 04:00 | flat_start_nr | 133.83 | 4 | 540 | 2025-10
2025-10-21 05:00 | flat_start_nr | 126.47 | 3 | 532 | 2025-10
2025-10-21 06:00 | flat_start_nr | 126.84 | 3 | 532 | 2025-10
2025-10-21 07:00 | flat_start_nr | 142.75 | 4 | 534 | 2025-10
2025-10-21 08:00 | flat_start_nr | 141.63 | 4 | 541 | 2025-10
2025-10-21 09:00 | flat_start_nr | 140.7 | 4 | 540 | 2025-10
2025-10-21 10:00 | flat_start_nr | 136.1 | 4 | 537 | 2025-10
2025-10-21 11:00 | flat_start_nr | 136.9 | 4 | 535 | 2025-10
2025-10-21 12:00 | flat_start_nr | 140.87 | 4 | 536 | 2025-10
2025-10-21 13:00 | flat_start_nr | 150.02 | 5 | 516 | 2025-10
2025-10-21 14:00 | flat_start_nr | 144.35 | 4 | 539 | 2025-10
2025-10-21 18:00 | flat_start_nr | 135.11 | 3 | 552 | 2025-10
2025-10-21 19:00 | flat_start_nr | 127.66 | 3 | 535 | 2025-10
2025-10-21 20:00 | flat_start_nr | 136.91 | 4 | 540 | 2025-10
2025-10-21 21:00 | flat_start_nr | 138.3 | 5 | 548 | 2025-10
2025-10-21 22:00 | flat_start_nr | 134.54 | 4 | 545 | 2025-10
2025-10-21 23:00 | flat_start_nr | 129.61 | 4 | 544 | 2025-10
2025-10-22 | flat_start_nr | 141.59 | 4 | 552 | 2025-10
2025-10-22 01:00 | flat_start_nr | 140.07 | 4 | 556 | 2025-10
2025-10-22 02:00 | flat_start_nr | 134.9 | 4 | 546 | 2025-10
2025-10-22 03:00 | flat_start_nr | 123.74 | 3 | 549 | 2025-10
2025-10-22 04:00 | flat_start_nr | 124.44 | 3 | 549 | 2025-10
2025-10-22 05:00 | flat_start_nr | 119.35 | 3 | 546 | 2025-10
2025-10-22 06:00 | flat_start_nr | 132.61 | 3 | 560 | 2025-10
2025-10-22 07:00 | flat_start_nr | 150.2 | 5 | 530 | 2025-10
2025-10-22 10:00 | flat_start_nr | 139.8 | 4 | 553 | 2025-10
2025-10-22 11:00 | flat_start_nr | 135.85 | 4 | 543 | 2025-10
2025-10-22 12:00 | flat_start_nr | 142.72 | 4 | 544 | 2025-10
2025-10-22 13:00 | flat_start_nr | 148.54 | 5 | 534 | 2025-10
2025-10-22 14:00 | flat_start_nr | 154.7 | 6 | 553 | 2025-10
2025-10-22 15:00 | flat_start_nr | 148.7 | 5 | 541 | 2025-10
2025-10-22 16:00 | flat_start_nr | 135.36 | 4 | 549 | 2025-10
2025-10-22 17:00 | flat_start_nr | 125.03 | 3 | 537 | 2025-10
2025-10-22 18:00 | flat_start_nr | 117.53 | 3 | 540 | 2025-10
2025-10-22 19:00 | flat_start_nr | 117.44 | 3 | 540 | 2025-10
2025-10-22 20:00 | flat_start_nr | 114.41 | 3 | 539 | 2025-10
2025-10-22 21:00 | flat_start_nr | 124.77 | 4 | 545 | 2025-10
2025-10-22 22:00 | flat_start_nr | 139.18 | 4 | 549 | 2025-10
2025-10-22 23:00 | flat_start_nr | 143.39 | 4 | 556 | 2025-10
2025-10-23 | flat_start_nr | 147.71 | 5 | 541 | 2025-10
2025-10-23 01:00 | flat_start_nr | 155.59 | 5 | 540 | 2025-10
2025-10-23 02:00 | flat_start_nr | 152.96 | 6 | 534 | 2025-10
2025-10-23 03:00 | flat_start_nr | 155.64 | 6 | 540 | 2025-10
2025-10-23 04:00 | flat_start_nr | 139.78 | 5 | 554 | 2025-10
2025-10-23 05:00 | flat_start_nr | 125.86 | 4 | 539 | 2025-10
2025-10-23 06:00 | flat_start_nr | 116.7 | 3 | 532 | 2025-10
2025-10-23 07:00 | flat_start_nr | 122.72 | 3 | 527 | 2025-10
2025-10-23 08:00 | flat_start_nr | 136.52 | 4 | 534 | 2025-10
2025-10-23 09:00 | flat_start_nr | 155.29 | 6 | 548 | 2025-10
2025-10-23 10:00 | flat_start_nr | 148.8 | 5 | 531 | 2025-10
2025-10-23 11:00 | flat_start_nr | 142.43 | 4 | 543 | 2025-10
2025-10-23 12:00 | flat_start_nr | 136.46 | 4 | 533 | 2025-10
2025-10-23 13:00 | flat_start_nr | 133.03 | 4 | 528 | 2025-10
2025-10-23 14:00 | flat_start_nr | 129.73 | 4 | 537 | 2025-10
2025-10-23 15:00 | flat_start_nr | 123.06 | 3 | 531 | 2025-10
2025-10-23 16:00 | flat_start_nr | 119.35 | 3 | 530 | 2025-10
2025-10-23 17:00 | flat_start_nr | 121.62 | 3 | 545 | 2025-10
2025-10-23 18:00 | flat_start_nr | 122.32 | 3 | 534 | 2025-10
2025-10-23 19:00 | flat_start_nr | 121.46 | 3 | 531 | 2025-10
2025-10-23 20:00 | flat_start_nr | 120.1 | 3 | 531 | 2025-10
2025-10-23 21:00 | flat_start_nr | 119.82 | 4 | 536 | 2025-10
2025-10-23 22:00 | flat_start_nr | 126.27 | 4 | 543 | 2025-10
2025-10-23 23:00 | flat_start_nr | 133.66 | 4 | 553 | 2025-10
2025-10-24 | flat_start_nr | 140.76 | 4 | 561 | 2025-10
2025-10-24 01:00 | flat_start_nr | 140.55 | 5 | 556 | 2025-10
2025-10-24 02:00 | flat_start_nr | 140.01 | 5 | 555 | 2025-10
2025-10-24 03:00 | flat_start_nr | 139.94 | 5 | 556 | 2025-10
2025-10-24 04:00 | flat_start_nr | 138.27 | 5 | 557 | 2025-10
2025-10-24 05:00 | flat_start_nr | 136.37 | 5 | 553 | 2025-10
2025-10-24 06:00 | flat_start_nr | 123.4 | 4 | 545 | 2025-10
2025-10-24 07:00 | flat_start_nr | 118.14 | 3 | 535 | 2025-10
2025-10-24 08:00 | flat_start_nr | 118.08 | 4 | 536 | 2025-10
2025-10-24 09:00 | flat_start_nr | 120.54 | 4 | 544 | 2025-10
2025-10-24 10:00 | flat_start_nr | 126.56 | 3 | 545 | 2025-10
2025-10-24 11:00 | flat_start_nr | 131.71 | 4 | 545 | 2025-10
2025-10-24 12:00 | flat_start_nr | 132.25 | 5 | 533 | 2025-10
2025-10-24 13:00 | flat_start_nr | 124.83 | 4 | 532 | 2025-10
2025-10-24 14:00 | flat_start_nr | 125.04 | 4 | 537 | 2025-10
2025-10-24 15:00 | flat_start_nr | 119.46 | 4 | 532 | 2025-10
2025-10-24 16:00 | flat_start_nr | 117.9 | 4 | 534 | 2025-10
2025-10-24 17:00 | flat_start_nr | 116.41 | 3 | 539 | 2025-10
2025-10-24 18:00 | flat_start_nr | 116.33 | 3 | 541 | 2025-10
2025-10-24 19:00 | flat_start_nr | 116.69 | 4 | 543 | 2025-10
2025-10-24 20:00 | flat_start_nr | 118.23 | 4 | 553 | 2025-10
2025-10-24 21:00 | flat_start_nr | 128.35 | 4 | 551 | 2025-10
2025-10-24 22:00 | flat_start_nr | 116.86 | 4 | 538 | 2025-10
2025-10-24 23:00 | flat_start_nr | 122.53 | 3 | 539 | 2025-10
2025-10-25 | flat_start_nr | 126.47 | 3 | 543 | 2025-10
2025-10-25 01:00 | flat_start_nr | 129.48 | 2 | 542 | 2025-10
2025-10-25 02:00 | flat_start_nr | 127.86 | 3 | 545 | 2025-10
2025-10-25 03:00 | flat_start_nr | 126.34 | 3 | 539 | 2025-10
2025-10-25 04:00 | flat_start_nr | 122.59 | 3 | 539 | 2025-10
2025-10-25 05:00 | flat_start_nr | 123.15 | 3 | 540 | 2025-10
2025-10-25 06:00 | flat_start_nr | 121.38 | 4 | 540 | 2025-10
2025-10-25 07:00 | flat_start_nr | 130.43 | 5 | 540 | 2025-10
2025-10-25 08:00 | flat_start_nr | 129.06 | 4 | 540 | 2025-10
2025-10-25 09:00 | flat_start_nr | 126.2 | 4 | 537 | 2025-10
2025-10-25 10:00 | flat_start_nr | 127.07 | 3 | 536 | 2025-10
2025-10-25 11:00 | flat_start_nr | 133.44 | 4 | 543 | 2025-10
2025-10-25 12:00 | flat_start_nr | 136.07 | 4 | 536 | 2025-10
2025-10-25 13:00 | flat_start_nr | 146.3 | 5 | 527 | 2025-10
2025-10-25 14:00 | flat_start_nr | 148.17 | 6 | 511 | 2025-10
2025-10-25 15:00 | flat_start_nr | 134.65 | 5 | 531 | 2025-10
2025-10-25 16:00 | flat_start_nr | 132.53 | 5 | 529 | 2025-10
2025-10-25 17:00 | flat_start_nr | 145.66 | 4 | 531 | 2025-10
2025-10-25 18:00 | flat_start_nr | 155.37 | 5 | 540 | 2025-10
2025-10-25 19:00 | flat_start_nr | 147.01 | 4 | 533 | 2025-10
2025-10-25 20:00 | flat_start_nr | 140.1 | 3 | 543 | 2025-10
2025-10-25 21:00 | flat_start_nr | 139.18 | 3 | 542 | 2025-10
2025-10-25 22:00 | flat_start_nr | 137.74 | 4 | 544 | 2025-10
2025-10-25 23:00 | flat_start_nr | 135.71 | 3 | 543 | 2025-10
2025-10-26 | flat_start_nr | 133.47 | 4 | 543 | 2025-10
2025-10-26 01:00 | flat_start_nr | 135.33 | 4 | 544 | 2025-10
2025-10-26 02:00 | flat_start_nr | 138.92 | 4 | 551 | 2025-10
2025-10-26 03:00 | flat_start_nr | 144.12 | 3 | 556 | 2025-10
2025-10-26 04:00 | flat_start_nr | 135.57 | 4 | 548 | 2025-10
2025-10-26 05:00 | flat_start_nr | 136.03 | 4 | 544 | 2025-10
2025-10-26 06:00 | flat_start_nr | 135.2 | 5 | 543 | 2025-10
2025-10-26 07:00 | flat_start_nr | 152.75 | 5 | 522 | 2025-10
2025-10-26 08:00 | flat_start_nr | 150.7 | 4 | 524 | 2025-10
2025-10-26 09:00 | flat_start_nr | 136.24 | 3 | 542 | 2025-10
2025-10-26 10:00 | flat_start_nr | 127.45 | 2 | 537 | 2025-10
2025-10-26 11:00 | flat_start_nr | 127.29 | 2 | 541 | 2025-10
2025-10-26 12:00 | flat_start_nr | 130.79 | 3 | 539 | 2025-10
2025-10-26 13:00 | flat_start_nr | 131.66 | 3 | 539 | 2025-10
2025-10-26 14:00 | flat_start_nr | 130.7 | 3 | 542 | 2025-10
2025-10-26 15:00 | flat_start_nr | 131.91 | 3 | 539 | 2025-10
2025-10-26 16:00 | flat_start_nr | 133.36 | 3 | 541 | 2025-10
2025-10-26 17:00 | flat_start_nr | 124.91 | 3 | 551 | 2025-10
2025-10-26 18:00 | flat_start_nr | 115.86 | 2 | 554 | 2025-10
2025-10-26 19:00 | flat_start_nr | 118.05 | 3 | 552 | 2025-10
2025-10-26 20:00 | flat_start_nr | 130.36 | 4 | 544 | 2025-10
2025-10-26 21:00 | flat_start_nr | 133.21 | 4 | 547 | 2025-10
2025-10-26 22:00 | flat_start_nr | 136.59 | 3 | 543 | 2025-10
2025-10-26 23:00 | flat_start_nr | 134.83 | 3 | 544 | 2025-10
2025-10-27 | flat_start_nr | 134.96 | 3 | 544 | 2025-10
2025-10-27 01:00 | flat_start_nr | 138.63 | 3 | 541 | 2025-10
2025-10-27 02:00 | flat_start_nr | 136.34 | 4 | 542 | 2025-10
2025-10-27 03:00 | flat_start_nr | 136.2 | 4 | 543 | 2025-10
2025-10-27 04:00 | flat_start_nr | 142.87 | 4 | 540 | 2025-10
2025-10-27 05:00 | flat_start_nr | 135.33 | 3 | 548 | 2025-10
2025-10-27 06:00 | flat_start_nr | 121.32 | 2 | 552 | 2025-10
2025-10-27 07:00 | flat_start_nr | 134.6 | 3 | 549 | 2025-10
2025-10-27 08:00 | flat_start_nr | 137.32 | 3 | 547 | 2025-10
2025-10-27 09:00 | flat_start_nr | 150.44 | 4 | 539 | 2025-10
2025-10-27 10:00 | flat_start_nr | 150.2 | 4 | 535 | 2025-10
2025-10-27 11:00 | flat_start_nr | 147.65 | 4 | 539 | 2025-10
2025-10-27 12:00 | flat_start_nr | 148.42 | 4 | 532 | 2025-10
2025-10-27 14:00 | flat_start_nr | 155.05 | 5 | 549 | 2025-10
2025-10-27 15:00 | flat_start_nr | 154.1 | 5 | 554 | 2025-10
2025-10-27 18:00 | flat_start_nr | 141.16 | 3 | 541 | 2025-10
2025-10-27 19:00 | flat_start_nr | 144.62 | 3 | 545 | 2025-10
2025-10-27 20:00 | flat_start_nr | 138.88 | 3 | 545 | 2025-10
2025-10-27 21:00 | flat_start_nr | 140.58 | 4 | 548 | 2025-10
2025-10-27 22:00 | flat_start_nr | 136.15 | 4 | 545 | 2025-10
2025-10-27 23:00 | flat_start_nr | 135.36 | 4 | 542 | 2025-10
2025-10-28 | flat_start_nr | 135.04 | 4 | 542 | 2025-10
2025-10-28 01:00 | flat_start_nr | 136.42 | 4 | 544 | 2025-10
2025-10-28 02:00 | flat_start_nr | 138.25 | 3 | 543 | 2025-10
2025-10-28 03:00 | flat_start_nr | 137.49 | 4 | 544 | 2025-10
2025-10-28 04:00 | flat_start_nr | 137.98 | 4 | 542 | 2025-10
2025-10-28 05:00 | flat_start_nr | 134.43 | 3 | 541 | 2025-10
2025-10-28 06:00 | flat_start_nr | 141.51 | 3 | 543 | 2025-10
2025-10-28 17:00 | flat_start_nr | 154.58 | 5 | 520 | 2025-10
2025-10-28 18:00 | flat_start_nr | 147.88 | 5 | 503 | 2025-10
2025-10-28 19:00 | flat_start_nr | 131.3 | 4 | 512 | 2025-10
2025-10-28 20:00 | flat_start_nr | 126.39 | 3 | 514 | 2025-10
2025-10-28 21:00 | flat_start_nr | 130.31 | 4 | 513 | 2025-10
2025-10-28 22:00 | flat_start_nr | 139.57 | 4 | 514 | 2025-10
2025-10-28 23:00 | flat_start_nr | 137.67 | 4 | 516 | 2025-10
2025-10-29 | flat_start_nr | 140.11 | 4 | 515 | 2025-10
2025-10-29 01:00 | flat_start_nr | 138.54 | 4 | 518 | 2025-10
2025-10-29 02:00 | flat_start_nr | 140.16 | 4 | 514 | 2025-10
2025-10-29 03:00 | flat_start_nr | 139.07 | 4 | 518 | 2025-10
2025-10-29 04:00 | flat_start_nr | 140.43 | 4 | 516 | 2025-10
2025-10-29 05:00 | flat_start_nr | 146.16 | 5 | 514 | 2025-10
2025-10-29 06:00 | flat_start_nr | 139.1 | 4 | 515 | 2025-10
2025-10-29 07:00 | flat_start_nr | 149.12 | 5 | 503 | 2025-10
2025-10-29 09:00 | flat_start_nr | 146.58 | 4 | 542 | 2025-10
2025-10-29 10:00 | flat_start_nr | 137.51 | 3 | 549 | 2025-10
2025-10-29 11:00 | flat_start_nr | 142.55 | 3 | 544 | 2025-10
2025-10-29 12:00 | flat_start_nr | 157.12 | 5 | 527 | 2025-10
2025-10-29 13:00 | flat_start_nr | 155.45 | 5 | 548 | 2025-10
2025-10-29 14:00 | flat_start_nr | 155.64 | 5 | 545 | 2025-10
2025-10-29 15:00 | flat_start_nr | 154.6 | 5 | 549 | 2025-10
2025-10-29 16:00 | flat_start_nr | 152.5 | 5 | 526 | 2025-10
2025-10-29 17:00 | flat_start_nr | 145.49 | 5 | 536 | 2025-10
2025-10-29 18:00 | flat_start_nr | 142.45 | 4 | 535 | 2025-10
2025-10-29 19:00 | flat_start_nr | 141.72 | 4 | 533 | 2025-10
2025-10-29 20:00 | flat_start_nr | 145.34 | 5 | 525 | 2025-10
2025-10-29 21:00 | flat_start_nr | 150.4 | 5 | 514 | 2025-10
2025-10-29 22:00 | flat_start_nr | 155.86 | 7 | 511 | 2025-10
2025-10-29 23:00 | flat_start_nr | 148.48 | 5 | 525 | 2025-10
2025-10-30 | flat_start_nr | 143.62 | 4 | 536 | 2025-10
2025-10-30 01:00 | flat_start_nr | 142.57 | 3 | 530 | 2025-10
2025-10-30 02:00 | flat_start_nr | 142.62 | 3 | 536 | 2025-10
2025-10-30 03:00 | flat_start_nr | 143.65 | 3 | 541 | 2025-10
2025-10-30 04:00 | flat_start_nr | 143.58 | 3 | 542 | 2025-10
2025-10-30 05:00 | flat_start_nr | 150.99 | 5 | 509 | 2025-10
2025-10-30 06:00 | flat_start_nr | 134.79 | 4 | 538 | 2025-10
2025-10-30 07:00 | flat_start_nr | 145.25 | 3 | 525 | 2025-10
2025-10-30 08:00 | flat_start_nr | 142.8 | 3 | 542 | 2025-10
2025-10-30 09:00 | flat_start_nr | 152.73 | 5 | 539 | 2025-10
2025-10-30 10:00 | flat_start_nr | 155.14 | 5 | 539 | 2025-10
2025-10-30 11:00 | flat_start_nr | 154.73 | 5 | 538 | 2025-10
2025-10-30 12:00 | flat_start_nr | 156.12 | 5 | 521 | 2025-10
2025-10-30 13:00 | flat_start_nr | 154.34 | 5 | 534 | 2025-10
2025-10-30 16:00 | flat_start_nr | 148.81 | 4 | 515 | 2025-10
2025-10-30 17:00 | flat_start_nr | 132.38 | 3 | 541 | 2025-10
2025-10-30 18:00 | flat_start_nr | 128.12 | 2 | 541 | 2025-10
2025-10-30 19:00 | flat_start_nr | 128.55 | 2 | 538 | 2025-10
2025-10-30 20:00 | flat_start_nr | 127.83 | 2 | 541 | 2025-10
2025-10-30 21:00 | flat_start_nr | 126.63 | 2 | 543 | 2025-10
2025-10-30 22:00 | flat_start_nr | 136.14 | 3 | 538 | 2025-10
2025-10-30 23:00 | flat_start_nr | 148.38 | 4 | 518 | 2025-10
2025-10-31 | flat_start_nr | 134.28 | 3 | 536 | 2025-10
2025-10-31 01:00 | flat_start_nr | 136.54 | 3 | 538 | 2025-10
2025-10-31 02:00 | flat_start_nr | 137.6 | 3 | 534 | 2025-10
2025-10-31 03:00 | flat_start_nr | 132.33 | 3 | 538 | 2025-10
2025-10-31 04:00 | flat_start_nr | 139.1 | 3 | 536 | 2025-10
2025-10-31 05:00 | flat_start_nr | 133.9 | 3 | 534 | 2025-10
2025-10-31 06:00 | flat_start_nr | 156.32 | 6 | 528 | 2025-10
2025-10-31 10:00 | flat_start_nr | 151.36 | 5 | 514 | 2025-10
2025-10-31 11:00 | flat_start_nr | 145.39 | 4 | 541 | 2025-10
2025-10-31 12:00 | flat_start_nr | 152.24 | 5 | 523 | 2025-10
2025-10-31 13:00 | flat_start_nr | 152.6 | 5 | 522 | 2025-10
2025-10-31 14:00 | flat_start_nr | 154.39 | 5 | 540 | 2025-10
2025-10-31 17:00 | flat_start_nr | 142.61 | 4 | 539 | 2025-10
2025-10-31 18:00 | flat_start_nr | 140.33 | 4 | 541 | 2025-10
2025-10-31 19:00 | flat_start_nr | 140.49 | 4 | 543 | 2025-10
2025-10-31 20:00 | flat_start_nr | 141.3 | 4 | 545 | 2025-10
2025-10-31 21:00 | flat_start_nr | 152.31 | 6 | 518 | 2025-10
2025-10-31 22:00 | flat_start_nr | 139.81 | 4 | 546 | 2025-10
2025-10-31 23:00 | flat_start_nr | 141.74 | 5 | 543 | 2025-10
2025-11-01 | flat_start_nr | 156.94 | 6 | 542 | 2025-11
2025-11-01 02:00 | flat_start_nr | 157.63 | 6 | 551 | 2025-11
2025-11-01 03:00 | flat_start_nr | 151.89 | 5 | 527 | 2025-11
2025-11-01 04:00 | flat_start_nr | 151.21 | 5 | 529 | 2025-11
2025-11-01 05:00 | flat_start_nr | 146.33 | 5 | 540 | 2025-11
2025-11-01 06:00 | flat_start_nr | 138.45 | 4 | 548 | 2025-11
2025-11-01 07:00 | flat_start_nr | 154.87 | 6 | 547 | 2025-11
2025-11-01 11:00 | flat_start_nr | 153.38 | 5 | 521 | 2025-11
2025-11-01 12:00 | flat_start_nr | 156.05 | 5 | 528 | 2025-11
2025-11-01 13:00 | flat_start_nr | 153.74 | 5 | 528 | 2025-11
2025-11-01 14:00 | flat_start_nr | 145.75 | 5 | 529 | 2025-11
2025-11-01 15:00 | flat_start_nr | 154.57 | 7 | 527 | 2025-11
2025-11-01 17:00 | flat_start_nr | 151.62 | 5 | 534 | 2025-11
2025-11-01 18:00 | flat_start_nr | 152.83 | 7 | 533 | 2025-11
2025-11-01 19:00 | flat_start_nr | 151.97 | 5 | 542 | 2025-11
2025-11-01 20:00 | flat_start_nr | 152.19 | 5 | 540 | 2025-11
2025-11-01 21:00 | flat_start_nr | 151.07 | 6 | 541 | 2025-11
2025-11-01 22:00 | flat_start_nr | 153.95 | 6 | 532 | 2025-11
2025-11-02 03:00 | flat_start_nr | 157.57 | 7 | 558 | 2025-11
2025-11-02 04:00 | flat_start_nr | 158.46 | 6 | 567 | 2025-11
2025-11-02 06:00 | flat_start_nr | 155.27 | 6 | 536 | 2025-11
2025-11-02 17:00 | flat_start_nr | 157.6 | 7 | 573 | 2025-11
2025-11-02 18:00 | flat_start_nr | 156.1 | 7 | 537 | 2025-11
2025-11-02 19:00 | flat_start_nr | 155.81 | 7 | 537 | 2025-11
2025-11-02 20:00 | flat_start_nr | 156.77 | 7 | 566 | 2025-11
2025-11-02 21:00 | flat_start_nr | 157.31 | 7 | 531 | 2025-11
2025-11-02 22:00 | flat_start_nr | 158.92 | 7 | 552 | 2025-11
2025-11-03 16:00 | flat_start_nr | 146.55 | 4 | 539 | 2025-11
2025-11-03 17:00 | flat_start_nr | 125 | 2 | 554 | 2025-11
2025-11-03 18:00 | flat_start_nr | 125.23 | 2 | 554 | 2025-11
2025-11-03 19:00 | flat_start_nr | 125.83 | 2 | 548 | 2025-11
2025-11-03 20:00 | flat_start_nr | 126.15 | 2 | 546 | 2025-11
2025-11-03 21:00 | flat_start_nr | 125.26 | 2 | 549 | 2025-11
2025-11-03 22:00 | flat_start_nr | 139.79 | 3 | 542 | 2025-11
2025-11-03 23:00 | flat_start_nr | 141.01 | 3 | 542 | 2025-11
2025-11-04 | flat_start_nr | 151.42 | 4 | 532 | 2025-11
2025-11-04 06:00 | flat_start_nr | 150.11 | 4 | 526 | 2025-11
2025-11-04 07:00 | flat_start_nr | 149.66 | 5 | 523 | 2025-11
2025-11-04 15:00 | flat_start_nr | 148.36 | 4 | 520 | 2025-11
2025-11-04 16:00 | flat_start_nr | 145.26 | 3 | 527 | 2025-11
2025-11-04 17:00 | flat_start_nr | 102.41 | 1 | 558 | 2025-11
2025-11-04 18:00 | flat_start_nr | 107.28 | 1 | 555 | 2025-11
2025-11-04 19:00 | flat_start_nr | 125.13 | 2 | 548 | 2025-11
2025-11-04 20:00 | flat_start_nr | 133.36 | 3 | 545 | 2025-11
2025-11-04 21:00 | flat_start_nr | 136.92 | 3 | 538 | 2025-11
2025-11-04 22:00 | flat_start_nr | 143.71 | 3 | 530 | 2025-11
2025-11-04 23:00 | flat_start_nr | 141.18 | 3 | 545 | 2025-11
2025-11-05 | flat_start_nr | 134.95 | 3 | 549 | 2025-11
2025-11-05 01:00 | flat_start_nr | 127.83 | 2 | 551 | 2025-11
2025-11-05 02:00 | flat_start_nr | 119.59 | 2 | 548 | 2025-11
2025-11-05 03:00 | flat_start_nr | 131.43 | 3 | 539 | 2025-11
2025-11-05 04:00 | flat_start_nr | 131.63 | 4 | 538 | 2025-11
2025-11-05 05:00 | flat_start_nr | 132.94 | 4 | 537 | 2025-11
2025-11-05 06:00 | flat_start_nr | 124 | 3 | 542 | 2025-11
2025-11-05 07:00 | flat_start_nr | 129.24 | 2 | 544 | 2025-11
2025-11-05 08:00 | flat_start_nr | 124.22 | 2 | 545 | 2025-11
2025-11-05 09:00 | flat_start_nr | 131.5 | 3 | 560 | 2025-11
2025-11-05 10:00 | flat_start_nr | 134.32 | 3 | 542 | 2025-11
2025-11-05 11:00 | flat_start_nr | 140.29 | 3 | 538 | 2025-11
2025-11-05 12:00 | flat_start_nr | 138.03 | 3 | 546 | 2025-11
2025-11-05 13:00 | flat_start_nr | 131.94 | 3 | 534 | 2025-11
2025-11-05 14:00 | flat_start_nr | 131.78 | 3 | 537 | 2025-11
2025-11-05 15:00 | flat_start_nr | 132.59 | 3 | 542 | 2025-11
2025-11-05 16:00 | flat_start_nr | 124.9 | 3 | 544 | 2025-11
2025-11-05 17:00 | flat_start_nr | 107.08 | 2 | 549 | 2025-11
2025-11-05 18:00 | flat_start_nr | 126.22 | 3 | 544 | 2025-11
2025-11-05 19:00 | flat_start_nr | 132.27 | 4 | 544 | 2025-11
2025-11-05 20:00 | flat_start_nr | 133.97 | 4 | 545 | 2025-11
2025-11-05 21:00 | flat_start_nr | 134.73 | 4 | 547 | 2025-11
2025-11-05 22:00 | flat_start_nr | 139.7 | 4 | 542 | 2025-11
2025-11-05 23:00 | flat_start_nr | 140.84 | 4 | 546 | 2025-11
2025-11-06 | normal_nr | 161.02 | 6 | 552 | 2025-11
2025-11-06 01:00 | flat_start_nr | 152.43 | 5 | 530 | 2025-11
2025-11-06 02:00 | flat_start_nr | 153.54 | 6 | 525 | 2025-11
2025-11-06 03:00 | flat_start_nr | 147.25 | 5 | 535 | 2025-11
2025-11-06 04:00 | flat_start_nr | 145.04 | 4 | 536 | 2025-11
2025-11-06 05:00 | flat_start_nr | 143.61 | 4 | 536 | 2025-11
2025-11-06 06:00 | flat_start_nr | 141.06 | 5 | 537 | 2025-11
2025-11-06 07:00 | flat_start_nr | 147.35 | 6 | 524 | 2025-11
2025-11-06 08:00 | flat_start_nr | 143.1 | 5 | 540 | 2025-11
2025-11-06 09:00 | flat_start_nr | 137.33 | 4 | 533 | 2025-11
2025-11-06 10:00 | flat_start_nr | 136.63 | 4 | 531 | 2025-11
2025-11-06 11:00 | flat_start_nr | 138.01 | 5 | 530 | 2025-11
2025-11-06 12:00 | flat_start_nr | 139.01 | 3 | 530 | 2025-11
2025-11-06 13:00 | flat_start_nr | 136.21 | 5 | 533 | 2025-11
2025-11-06 14:00 | flat_start_nr | 137.66 | 5 | 536 | 2025-11
2025-11-06 15:00 | flat_start_nr | 138.35 | 5 | 534 | 2025-11
2025-11-06 16:00 | flat_start_nr | 143.64 | 3 | 537 | 2025-11
2025-11-06 17:00 | flat_start_nr | 121.96 | 2 | 542 | 2025-11
2025-11-06 18:00 | flat_start_nr | 127.27 | 3 | 540 | 2025-11
2025-11-06 19:00 | flat_start_nr | 124.52 | 2 | 546 | 2025-11
2025-11-06 20:00 | flat_start_nr | 127.7 | 2 | 547 | 2025-11
2025-11-06 21:00 | flat_start_nr | 117.73 | 2 | 549 | 2025-11
2025-11-06 22:00 | flat_start_nr | 118.39 | 2 | 554 | 2025-11
2025-11-06 23:00 | flat_start_nr | 120.25 | 2 | 555 | 2025-11
2025-11-07 | flat_start_nr | 126.62 | 2 | 555 | 2025-11
2025-11-07 01:00 | flat_start_nr | 123.6 | 2 | 554 | 2025-11
2025-11-07 02:00 | flat_start_nr | 128.86 | 2 | 552 | 2025-11
2025-11-07 03:00 | flat_start_nr | 139.72 | 3 | 548 | 2025-11
2025-11-07 04:00 | flat_start_nr | 141.16 | 3 | 546 | 2025-11
2025-11-07 05:00 | flat_start_nr | 140.63 | 4 | 543 | 2025-11
2025-11-07 06:00 | flat_start_nr | 138.89 | 3 | 538 | 2025-11
2025-11-07 07:00 | flat_start_nr | 132.98 | 4 | 540 | 2025-11
2025-11-07 08:00 | flat_start_nr | 132.74 | 3 | 537 | 2025-11
2025-11-07 09:00 | flat_start_nr | 131.89 | 4 | 535 | 2025-11
2025-11-07 10:00 | flat_start_nr | 139.56 | 3 | 539 | 2025-11
2025-11-07 11:00 | flat_start_nr | 141.32 | 3 | 536 | 2025-11
2025-11-07 12:00 | flat_start_nr | 141.41 | 3 | 530 | 2025-11
2025-11-07 13:00 | flat_start_nr | 139.34 | 3 | 540 | 2025-11
2025-11-07 14:00 | flat_start_nr | 136.11 | 3 | 540 | 2025-11
2025-11-07 15:00 | flat_start_nr | 133.91 | 4 | 540 | 2025-11
2025-11-07 16:00 | flat_start_nr | 135.64 | 5 | 544 | 2025-11
2025-11-07 17:00 | flat_start_nr | 142.34 | 5 | 544 | 2025-11
2025-11-07 18:00 | flat_start_nr | 139.29 | 4 | 540 | 2025-11
2025-11-07 19:00 | flat_start_nr | 143.68 | 4 | 540 | 2025-11
2025-11-07 20:00 | flat_start_nr | 143.6 | 4 | 540 | 2025-11
2025-11-07 21:00 | flat_start_nr | 145.01 | 3 | 537 | 2025-11
2025-11-07 22:00 | flat_start_nr | 143.55 | 3 | 540 | 2025-11
2025-11-07 23:00 | flat_start_nr | 152.47 | 5 | 519 | 2025-11
2025-11-08 | flat_start_nr | 141.92 | 3 | 551 | 2025-11
2025-11-08 01:00 | flat_start_nr | 126.4 | 2 | 545 | 2025-11
2025-11-08 02:00 | flat_start_nr | 133.47 | 3 | 543 | 2025-11
2025-11-08 03:00 | flat_start_nr | 131.15 | 3 | 543 | 2025-11
2025-11-08 04:00 | flat_start_nr | 131.44 | 3 | 545 | 2025-11
2025-11-08 05:00 | flat_start_nr | 136.94 | 3 | 544 | 2025-11
2025-11-08 06:00 | flat_start_nr | 144.84 | 3 | 546 | 2025-11
2025-11-08 07:00 | flat_start_nr | 144.98 | 3 | 551 | 2025-11
2025-11-08 17:00 | flat_start_nr | 149.68 | 4 | 525 | 2025-11
2025-11-08 18:00 | flat_start_nr | 148.18 | 4 | 519 | 2025-11
2025-11-08 20:00 | flat_start_nr | 144.93 | 3 | 533 | 2025-11
2025-11-08 21:00 | flat_start_nr | 143.58 | 3 | 540 | 2025-11
2025-11-08 22:00 | flat_start_nr | 143.87 | 3 | 542 | 2025-11
2025-11-08 23:00 | flat_start_nr | 146.8 | 4 | 527 | 2025-11
2025-11-09 | flat_start_nr | 150.45 | 4 | 511 | 2025-11
2025-11-09 01:00 | flat_start_nr | 128.89 | 2 | 540 | 2025-11
2025-11-09 02:00 | flat_start_nr | 127.25 | 3 | 542 | 2025-11
2025-11-09 03:00 | flat_start_nr | 145.92 | 5 | 534 | 2025-11
2025-11-09 04:00 | flat_start_nr | 137.67 | 4 | 542 | 2025-11
2025-11-09 05:00 | flat_start_nr | 136.18 | 4 | 542 | 2025-11
2025-11-09 06:00 | flat_start_nr | 135 | 4 | 542 | 2025-11
2025-11-09 07:00 | flat_start_nr | 144.14 | 4 | 537 | 2025-11
2025-11-09 08:00 | flat_start_nr | 152.06 | 5 | 522 | 2025-11
2025-11-09 09:00 | flat_start_nr | 150.67 | 7 | 525 | 2025-11
2025-11-09 10:00 | flat_start_nr | 150.13 | 6 | 524 | 2025-11
2025-11-09 11:00 | flat_start_nr | 147.28 | 6 | 523 | 2025-11
2025-11-09 12:00 | flat_start_nr | 149.34 | 6 | 525 | 2025-11
2025-11-09 13:00 | flat_start_nr | 145.92 | 5 | 537 | 2025-11
2025-11-09 14:00 | flat_start_nr | 148.93 | 6 | 535 | 2025-11
2025-11-09 15:00 | flat_start_nr | 149.69 | 5 | 535 | 2025-11
2025-11-09 16:00 | flat_start_nr | 138.87 | 5 | 545 | 2025-11
2025-11-09 17:00 | flat_start_nr | 127.29 | 4 | 550 | 2025-11
2025-11-09 18:00 | flat_start_nr | 133.94 | 5 | 547 | 2025-11
2025-11-09 19:00 | flat_start_nr | 130.55 | 5 | 547 | 2025-11
2025-11-09 20:00 | flat_start_nr | 129.48 | 4 | 548 | 2025-11
2025-11-09 21:00 | flat_start_nr | 127.76 | 5 | 546 | 2025-11
2025-11-09 22:00 | flat_start_nr | 136.89 | 7 | 545 | 2025-11
2025-11-10 06:00 | flat_start_nr | 139.4 | 5 | 547 | 2025-11
2025-11-10 07:00 | flat_start_nr | 132.97 | 5 | 547 | 2025-11
2025-11-10 08:00 | flat_start_nr | 137.27 | 4 | 539 | 2025-11
2025-11-10 09:00 | flat_start_nr | 140.33 | 5 | 545 | 2025-11
2025-11-10 11:00 | flat_start_nr | 126.83 | 5 | 538 | 2025-11
2025-11-10 12:00 | flat_start_nr | 142.88 | 6 | 551 | 2025-11
2025-11-10 13:00 | flat_start_nr | 140.65 | 5 | 559 | 2025-11
2025-11-10 14:00 | flat_start_nr | 138.62 | 4 | 559 | 2025-11
2025-11-10 15:00 | flat_start_nr | 145.56 | 6 | 558 | 2025-11
2025-11-10 16:00 | flat_start_nr | 150.28 | 6 | 533 | 2025-11
2025-11-10 17:00 | flat_start_nr | 132.96 | 6 | 550 | 2025-11
2025-11-10 18:00 | flat_start_nr | 126.67 | 5 | 547 | 2025-11
2025-11-10 19:00 | flat_start_nr | 126.96 | 5 | 549 | 2025-11
2025-11-10 20:00 | flat_start_nr | 127.24 | 5 | 547 | 2025-11
2025-11-10 21:00 | flat_start_nr | 124.5 | 5 | 550 | 2025-11
2025-11-10 22:00 | flat_start_nr | 126.78 | 5 | 549 | 2025-11
2025-11-10 23:00 | flat_start_nr | 123.5 | 4 | 550 | 2025-11
2025-11-11 | flat_start_nr | 128.01 | 4 | 545 | 2025-11
2025-11-11 01:00 | flat_start_nr | 137.06 | 5 | 550 | 2025-11
2025-11-11 02:00 | flat_start_nr | 117.68 | 4 | 546 | 2025-11
2025-11-11 03:00 | flat_start_nr | 126.1 | 5 | 544 | 2025-11
2025-11-11 04:00 | flat_start_nr | 116.91 | 4 | 542 | 2025-11
2025-11-11 05:00 | flat_start_nr | 118.22 | 3 | 544 | 2025-11
2025-11-11 06:00 | flat_start_nr | 126.32 | 3 | 535 | 2025-11
2025-11-11 07:00 | flat_start_nr | 133.65 | 5 | 528 | 2025-11
2025-11-11 08:00 | flat_start_nr | 144.57 | 4 | 524 | 2025-11
2025-11-11 09:00 | flat_start_nr | 143.25 | 4 | 538 | 2025-11
2025-11-11 10:00 | flat_start_nr | 146.22 | 4 | 524 | 2025-11
2025-11-11 11:00 | flat_start_nr | 136.55 | 4 | 533 | 2025-11
2025-11-11 12:00 | flat_start_nr | 144.68 | 3 | 530 | 2025-11
2025-11-11 13:00 | flat_start_nr | 147.98 | 5 | 528 | 2025-11
2025-11-11 14:00 | flat_start_nr | 148.87 | 5 | 518 | 2025-11
2025-11-11 15:00 | flat_start_nr | 148.15 | 5 | 513 | 2025-11
2025-11-11 16:00 | flat_start_nr | 135.89 | 4 | 532 | 2025-11
2025-11-11 17:00 | flat_start_nr | 118.95 | 3 | 533 | 2025-11
2025-11-11 18:00 | flat_start_nr | 119.13 | 3 | 537 | 2025-11
2025-11-11 19:00 | flat_start_nr | 121.39 | 3 | 533 | 2025-11
2025-11-11 20:00 | flat_start_nr | 128.25 | 3 | 533 | 2025-11
2025-11-11 21:00 | flat_start_nr | 126.07 | 4 | 540 | 2025-11
2025-11-11 22:00 | flat_start_nr | 127.38 | 4 | 534 | 2025-11
2025-11-11 23:00 | flat_start_nr | 128.88 | 4 | 537 | 2025-11
2025-11-12 | flat_start_nr | 130.98 | 5 | 536 | 2025-11
2025-11-12 01:00 | flat_start_nr | 132.82 | 4 | 541 | 2025-11
2025-11-12 02:00 | flat_start_nr | 135.39 | 4 | 531 | 2025-11
2025-11-12 03:00 | flat_start_nr | 125.09 | 3 | 539 | 2025-11
2025-11-12 04:00 | flat_start_nr | 124.01 | 3 | 541 | 2025-11
2025-11-12 05:00 | flat_start_nr | 126.3 | 2 | 543 | 2025-11
2025-11-12 06:00 | flat_start_nr | 130.17 | 3 | 542 | 2025-11
2025-11-12 07:00 | flat_start_nr | 131.38 | 3 | 532 | 2025-11
2025-11-12 09:00 | flat_start_nr | 148.94 | 5 | 526 | 2025-11
2025-11-12 12:00 | flat_start_nr | 152.33 | 6 | 522 | 2025-11
2025-11-12 15:00 | flat_start_nr | 148.33 | 6 | 508 | 2025-11
2025-11-12 16:00 | flat_start_nr | 135.04 | 4 | 533 | 2025-11
2025-11-12 17:00 | flat_start_nr | 120.12 | 2 | 534 | 2025-11
2025-11-12 18:00 | flat_start_nr | 116.84 | 3 | 537 | 2025-11
2025-11-12 19:00 | flat_start_nr | 118.97 | 3 | 536 | 2025-11
2025-11-12 23:00 | flat_start_nr | 158.05 | 6 | 544 | 2025-11
2025-11-13 | flat_start_nr | 134.09 | 4 | 538 | 2025-11
2025-11-13 01:00 | flat_start_nr | 135.28 | 4 | 537 | 2025-11
2025-11-13 02:00 | flat_start_nr | 140.41 | 5 | 537 | 2025-11
2025-11-13 03:00 | flat_start_nr | 146.04 | 6 | 539 | 2025-11
2025-11-13 05:00 | flat_start_nr | 151.44 | 6 | 528 | 2025-11
2025-11-13 06:00 | flat_start_nr | 139.83 | 6 | 541 | 2025-11
2025-11-13 07:00 | flat_start_nr | 144.19 | 6 | 540 | 2025-11
2025-11-13 17:00 | flat_start_nr | 146.62 | 7 | 539 | 2025-11
2025-11-13 18:00 | flat_start_nr | 146.53 | 7 | 536 | 2025-11
2025-11-13 19:00 | flat_start_nr | 146.24 | 6 | 532 | 2025-11
2025-11-13 20:00 | flat_start_nr | 148.71 | 6 | 527 | 2025-11
2025-11-13 21:00 | flat_start_nr | 139.17 | 6 | 538 | 2025-11
2025-11-13 22:00 | flat_start_nr | 144.64 | 6 | 545 | 2025-11
2025-11-14 02:00 | flat_start_nr | 153.18 | 6 | 526 | 2025-11
2025-11-14 03:00 | flat_start_nr | 135.28 | 4 | 541 | 2025-11
2025-11-14 04:00 | flat_start_nr | 129.91 | 4 | 538 | 2025-11
2025-11-14 05:00 | flat_start_nr | 129.32 | 3 | 533 | 2025-11
2025-11-14 06:00 | flat_start_nr | 120.15 | 3 | 538 | 2025-11
2025-11-14 07:00 | flat_start_nr | 119.96 | 3 | 537 | 2025-11
2025-11-14 08:00 | flat_start_nr | 127.77 | 3 | 528 | 2025-11
2025-11-14 09:00 | flat_start_nr | 123.57 | 3 | 520 | 2025-11
2025-11-14 10:00 | flat_start_nr | 121.18 | 3 | 528 | 2025-11
2025-11-14 11:00 | flat_start_nr | 130.79 | 4 | 536 | 2025-11
2025-11-14 12:00 | flat_start_nr | 120.93 | 3 | 535 | 2025-11
2025-11-14 13:00 | flat_start_nr | 121.98 | 3 | 532 | 2025-11
2025-11-14 14:00 | flat_start_nr | 126.12 | 3 | 528 | 2025-11
2025-11-14 15:00 | flat_start_nr | 120.11 | 3 | 534 | 2025-11
2025-11-14 16:00 | flat_start_nr | 116.28 | 3 | 541 | 2025-11
2025-11-14 17:00 | flat_start_nr | 115.95 | 2 | 535 | 2025-11
2025-11-14 18:00 | flat_start_nr | 116.12 | 2 | 532 | 2025-11
2025-11-14 19:00 | flat_start_nr | 115.43 | 2 | 541 | 2025-11
2025-11-14 20:00 | flat_start_nr | 115.14 | 2 | 545 | 2025-11
2025-11-14 21:00 | flat_start_nr | 121.88 | 3 | 552 | 2025-11
2025-11-14 22:00 | flat_start_nr | 124.38 | 3 | 549 | 2025-11
2025-11-14 23:00 | flat_start_nr | 129.21 | 3 | 555 | 2025-11
2025-11-15 | flat_start_nr | 132.92 | 4 | 548 | 2025-11
2025-11-15 01:00 | flat_start_nr | 136.67 | 4 | 550 | 2025-11
2025-11-15 02:00 | flat_start_nr | 137.68 | 4 | 545 | 2025-11
2025-11-15 03:00 | flat_start_nr | 144.66 | 5 | 543 | 2025-11
2025-11-15 04:00 | flat_start_nr | 153.23 | 7 | 530 | 2025-11
2025-11-15 05:00 | flat_start_nr | 149.3 | 7 | 542 | 2025-11
2025-11-15 06:00 | flat_start_nr | 143.32 | 7 | 559 | 2025-11
2025-11-15 07:00 | flat_start_nr | 132.41 | 5 | 542 | 2025-11
2025-11-15 08:00 | flat_start_nr | 132.3 | 5 | 532 | 2025-11
2025-11-15 09:00 | flat_start_nr | 145.11 | 5 | 541 | 2025-11
2025-11-15 12:00 | flat_start_nr | 154.89 | 6 | 530 | 2025-11
2025-11-15 15:00 | flat_start_nr | 138.08 | 4 | 538 | 2025-11
2025-11-15 16:00 | flat_start_nr | 124.56 | 3 | 535 | 2025-11
2025-11-15 17:00 | flat_start_nr | 108.82 | 2 | 535 | 2025-11
2025-11-15 18:00 | flat_start_nr | 120.57 | 3 | 530 | 2025-11
2025-11-15 19:00 | flat_start_nr | 121.77 | 3 | 534 | 2025-11
2025-11-15 20:00 | flat_start_nr | 120.53 | 3 | 536 | 2025-11
2025-11-15 21:00 | flat_start_nr | 128.04 | 3 | 545 | 2025-11
2025-11-15 22:00 | flat_start_nr | 142.28 | 4 | 560 | 2025-11
2025-11-15 23:00 | flat_start_nr | 131.59 | 4 | 552 | 2025-11
2025-11-16 | flat_start_nr | 129.37 | 3 | 548 | 2025-11
2025-11-16 01:00 | flat_start_nr | 123.17 | 3 | 544 | 2025-11
2025-11-16 02:00 | flat_start_nr | 119.38 | 3 | 541 | 2025-11
2025-11-16 03:00 | flat_start_nr | 123.37 | 3 | 540 | 2025-11
2025-11-16 04:00 | flat_start_nr | 143.25 | 4 | 550 | 2025-11
2025-11-16 05:00 | flat_start_nr | 155.34 | 7 | 531 | 2025-11
2025-11-16 06:00 | flat_start_nr | 144.55 | 6 | 554 | 2025-11
2025-11-16 07:00 | flat_start_nr | 134.17 | 6 | 534 | 2025-11
2025-11-16 08:00 | flat_start_nr | 148.42 | 7 | 527 | 2025-11
2025-11-16 09:00 | flat_start_nr | 155.43 | 7 | 542 | 2025-11
2025-11-16 10:00 | flat_start_nr | 152.94 | 6 | 520 | 2025-11
2025-11-16 11:00 | flat_start_nr | 146.3 | 5 | 534 | 2025-11
2025-11-16 12:00 | flat_start_nr | 143.44 | 4 | 542 | 2025-11
2025-11-16 13:00 | flat_start_nr | 143.31 | 4 | 542 | 2025-11
2025-11-16 14:00 | flat_start_nr | 143.6 | 4 | 544 | 2025-11
2025-11-16 15:00 | flat_start_nr | 143.42 | 4 | 549 | 2025-11
2025-11-16 16:00 | flat_start_nr | 144.79 | 4 | 541 | 2025-11
2025-11-16 17:00 | flat_start_nr | 117.56 | 4 | 542 | 2025-11
2025-11-16 18:00 | flat_start_nr | 129.09 | 4 | 548 | 2025-11
2025-11-16 19:00 | flat_start_nr | 135.29 | 5 | 543 | 2025-11
2025-11-16 20:00 | flat_start_nr | 127.77 | 4 | 547 | 2025-11
2025-11-16 21:00 | flat_start_nr | 126.67 | 4 | 543 | 2025-11
2025-11-16 22:00 | flat_start_nr | 134.2 | 5 | 546 | 2025-11
2025-11-16 23:00 | flat_start_nr | 142.79 | 5 | 550 | 2025-11
2025-11-17 | flat_start_nr | 151.63 | 6 | 544 | 2025-11
2025-11-17 01:00 | flat_start_nr | 157.64 | 7 | 563 | 2025-11
2025-11-17 02:00 | flat_start_nr | 156.21 | 7 | 569 | 2025-11
2025-11-17 03:00 | flat_start_nr | 156.14 | 7 | 535 | 2025-11
2025-11-17 04:00 | flat_start_nr | 147.43 | 6 | 552 | 2025-11
2025-11-17 05:00 | flat_start_nr | 141.31 | 5 | 553 | 2025-11
2025-11-17 06:00 | flat_start_nr | 135.95 | 5 | 554 | 2025-11
2025-11-17 07:00 | flat_start_nr | 138.22 | 5 | 550 | 2025-11
2025-11-17 08:00 | flat_start_nr | 151.27 | 6 | 527 | 2025-11
2025-11-17 09:00 | flat_start_nr | 151.62 | 6 | 528 | 2025-11
2025-11-17 10:00 | flat_start_nr | 137.45 | 5 | 543 | 2025-11
2025-11-17 11:00 | flat_start_nr | 132.68 | 5 | 532 | 2025-11
2025-11-17 12:00 | flat_start_nr | 133.33 | 5 | 527 | 2025-11
2025-11-17 13:00 | flat_start_nr | 140.03 | 5 | 520 | 2025-11
2025-11-17 14:00 | flat_start_nr | 137.17 | 5 | 534 | 2025-11
2025-11-17 15:00 | flat_start_nr | 148.38 | 4 | 518 | 2025-11
2025-11-17 16:00 | flat_start_nr | 139.16 | 3 | 542 | 2025-11
2025-11-17 17:00 | flat_start_nr | 122.84 | 2 | 543 | 2025-11
2025-11-17 18:00 | flat_start_nr | 145.81 | 4 | 540 | 2025-11
2025-11-17 19:00 | flat_start_nr | 134.99 | 3 | 548 | 2025-11
2025-11-17 20:00 | flat_start_nr | 146.41 | 4 | 543 | 2025-11
2025-11-17 23:00 | normal_nr | 159.75 | 6 | 551 | 2025-11
2025-11-18 | flat_start_nr | 153.1 | 6 | 530 | 2025-11
2025-11-18 01:00 | flat_start_nr | 144.85 | 4 | 543 | 2025-11
2025-11-18 02:00 | flat_start_nr | 134.92 | 4 | 543 | 2025-11
2025-11-18 03:00 | flat_start_nr | 132.37 | 4 | 539 | 2025-11
2025-11-18 04:00 | flat_start_nr | 124 | 4 | 541 | 2025-11
2025-11-18 05:00 | flat_start_nr | 133.54 | 5 | 535 | 2025-11
2025-11-18 06:00 | flat_start_nr | 132.46 | 3 | 540 | 2025-11
2025-11-18 07:00 | flat_start_nr | 128.88 | 2 | 550 | 2025-11
2025-11-18 08:00 | flat_start_nr | 141.12 | 3 | 557 | 2025-11
2025-11-18 09:00 | flat_start_nr | 152.68 | 5 | 537 | 2025-11
2025-11-18 11:00 | flat_start_nr | 135.77 | 4 | 539 | 2025-11
2025-11-18 12:00 | flat_start_nr | 128.39 | 4 | 542 | 2025-11
2025-11-18 13:00 | flat_start_nr | 126.15 | 4 | 541 | 2025-11
2025-11-18 14:00 | flat_start_nr | 128.87 | 3 | 534 | 2025-11
2025-11-18 15:00 | flat_start_nr | 138 | 4 | 532 | 2025-11
2025-11-18 16:00 | flat_start_nr | 123.04 | 4 | 542 | 2025-11
2025-11-18 17:00 | flat_start_nr | 114.53 | 4 | 546 | 2025-11
2025-11-18 18:00 | flat_start_nr | 115.49 | 3 | 543 | 2025-11
2025-11-18 19:00 | flat_start_nr | 127.42 | 3 | 545 | 2025-11
2025-11-18 20:00 | flat_start_nr | 136.02 | 4 | 547 | 2025-11
2025-11-18 21:00 | flat_start_nr | 140.25 | 4 | 543 | 2025-11
2025-11-18 22:00 | flat_start_nr | 129.3 | 4 | 537 | 2025-11
2025-11-18 23:00 | flat_start_nr | 137.24 | 4 | 535 | 2025-11
2025-11-19 | flat_start_nr | 130.39 | 4 | 539 | 2025-11
2025-11-19 01:00 | flat_start_nr | 123.21 | 4 | 546 | 2025-11
2025-11-19 02:00 | flat_start_nr | 126.71 | 4 | 538 | 2025-11
2025-11-19 03:00 | flat_start_nr | 131.01 | 4 | 538 | 2025-11
2025-11-19 04:00 | flat_start_nr | 137.36 | 4 | 540 | 2025-11
2025-11-19 05:00 | flat_start_nr | 133.62 | 4 | 547 | 2025-11
2025-11-19 06:00 | flat_start_nr | 130.06 | 4 | 546 | 2025-11
2025-11-19 07:00 | flat_start_nr | 131.73 | 4 | 546 | 2025-11
2025-11-19 08:00 | flat_start_nr | 144.66 | 4 | 530 | 2025-11
2025-11-19 09:00 | flat_start_nr | 154.36 | 6 | 548 | 2025-11
2025-11-19 10:00 | flat_start_nr | 155.18 | 6 | 533 | 2025-11
2025-11-19 11:00 | flat_start_nr | 150.88 | 6 | 524 | 2025-11
2025-11-19 12:00 | flat_start_nr | 153.74 | 6 | 544 | 2025-11
2025-11-19 13:00 | flat_start_nr | 154.65 | 6 | 531 | 2025-11
2025-11-19 15:00 | flat_start_nr | 150.99 | 5 | 524 | 2025-11
2025-11-19 16:00 | flat_start_nr | 147.42 | 4 | 543 | 2025-11
2025-11-19 17:00 | flat_start_nr | 129.32 | 2 | 560 | 2025-11
2025-11-19 18:00 | flat_start_nr | 124.11 | 2 | 550 | 2025-11
2025-11-19 19:00 | flat_start_nr | 119.47 | 3 | 554 | 2025-11
2025-11-19 20:00 | flat_start_nr | 113.43 | 2 | 548 | 2025-11
2025-11-19 21:00 | flat_start_nr | 119.08 | 3 | 544 | 2025-11
2025-11-19 22:00 | flat_start_nr | 129.66 | 4 | 548 | 2025-11
2025-11-19 23:00 | flat_start_nr | 134.91 | 4 | 543 | 2025-11
2025-11-20 | flat_start_nr | 141.41 | 4 | 544 | 2025-11
2025-11-20 01:00 | flat_start_nr | 135.1 | 4 | 543 | 2025-11
2025-11-20 02:00 | flat_start_nr | 129.49 | 3 | 543 | 2025-11
2025-11-20 03:00 | flat_start_nr | 126.64 | 4 | 541 | 2025-11
2025-11-20 04:00 | flat_start_nr | 134.26 | 4 | 541 | 2025-11
2025-11-20 05:00 | flat_start_nr | 138.44 | 5 | 543 | 2025-11
2025-11-20 06:00 | flat_start_nr | 129.45 | 4 | 538 | 2025-11
2025-11-20 07:00 | flat_start_nr | 124.57 | 4 | 550 | 2025-11
2025-11-20 08:00 | flat_start_nr | 133.62 | 4 | 543 | 2025-11
2025-11-20 09:00 | flat_start_nr | 140.1 | 4 | 540 | 2025-11
2025-11-20 10:00 | flat_start_nr | 147.07 | 5 | 532 | 2025-11
2025-11-20 11:00 | flat_start_nr | 150.85 | 5 | 519 | 2025-11
2025-11-20 12:00 | flat_start_nr | 154.72 | 6 | 521 | 2025-11
2025-11-20 14:00 | flat_start_nr | 155.25 | 6 | 545 | 2025-11
2025-11-20 15:00 | flat_start_nr | 140.57 | 4 | 544 | 2025-11
2025-11-20 16:00 | flat_start_nr | 135.55 | 4 | 539 | 2025-11
2025-11-20 17:00 | flat_start_nr | 137.01 | 6 | 541 | 2025-11
2025-11-20 18:00 | flat_start_nr | 150.57 | 6 | 534 | 2025-11
2025-11-20 19:00 | flat_start_nr | 154.21 | 7 | 538 | 2025-11
2025-11-20 20:00 | flat_start_nr | 139.47 | 6 | 550 | 2025-11
2025-11-20 21:00 | flat_start_nr | 135.72 | 6 | 547 | 2025-11
2025-11-20 22:00 | flat_start_nr | 138.36 | 6 | 549 | 2025-11
2025-11-20 23:00 | flat_start_nr | 140.8 | 6 | 549 | 2025-11
2025-11-21 | flat_start_nr | 151.11 | 7 | 538 | 2025-11
2025-11-21 01:00 | flat_start_nr | 143.55 | 6 | 552 | 2025-11
2025-11-21 02:00 | flat_start_nr | 139.91 | 6 | 543 | 2025-11
2025-11-21 03:00 | flat_start_nr | 139.94 | 6 | 544 | 2025-11
2025-11-21 04:00 | flat_start_nr | 139.75 | 5 | 542 | 2025-11
2025-11-21 05:00 | flat_start_nr | 139.45 | 5 | 545 | 2025-11
2025-11-21 06:00 | flat_start_nr | 123.18 | 5 | 541 | 2025-11
2025-11-21 07:00 | flat_start_nr | 124.03 | 5 | 542 | 2025-11
2025-11-21 08:00 | flat_start_nr | 133.1 | 5 | 531 | 2025-11
2025-11-21 09:00 | flat_start_nr | 139.32 | 5 | 543 | 2025-11
2025-11-21 10:00 | flat_start_nr | 147.38 | 6 | 535 | 2025-11
2025-11-21 11:00 | flat_start_nr | 150.02 | 7 | 527 | 2025-11
2025-11-21 12:00 | flat_start_nr | 145.57 | 7 | 533 | 2025-11
2025-11-21 13:00 | flat_start_nr | 142.2 | 6 | 541 | 2025-11
2025-11-21 14:00 | flat_start_nr | 136.29 | 7 | 532 | 2025-11
2025-11-21 16:00 | flat_start_nr | 131.46 | 7 | 537 | 2025-11
2025-11-21 17:00 | flat_start_nr | 128.72 | 6 | 546 | 2025-11
2025-11-21 18:00 | flat_start_nr | 128.52 | 6 | 546 | 2025-11
2025-11-21 19:00 | flat_start_nr | 129.11 | 6 | 543 | 2025-11
2025-11-21 20:00 | flat_start_nr | 129.34 | 6 | 542 | 2025-11
2025-11-21 21:00 | flat_start_nr | 127.01 | 4 | 548 | 2025-11
2025-11-21 22:00 | flat_start_nr | 130.92 | 5 | 549 | 2025-11
2025-11-21 23:00 | flat_start_nr | 156.02 | 7 | 533 | 2025-11
2025-11-22 | flat_start_nr | 144.77 | 5 | 555 | 2025-11
2025-11-22 01:00 | flat_start_nr | 147.49 | 6 | 550 | 2025-11
2025-11-22 02:00 | flat_start_nr | 141 | 5 | 553 | 2025-11
2025-11-22 03:00 | flat_start_nr | 139.7 | 4 | 548 | 2025-11
2025-11-22 04:00 | flat_start_nr | 144.79 | 4 | 552 | 2025-11
2025-11-22 05:00 | flat_start_nr | 147.45 | 5 | 548 | 2025-11
2025-11-22 06:00 | flat_start_nr | 150.7 | 5 | 537 | 2025-11
2025-11-22 07:00 | flat_start_nr | 151.7 | 5 | 535 | 2025-11
2025-11-22 17:00 | flat_start_nr | 132.55 | 6 | 541 | 2025-11
2025-11-22 18:00 | flat_start_nr | 142.51 | 6 | 545 | 2025-11
2025-11-22 19:00 | flat_start_nr | 151.78 | 7 | 534 | 2025-11
2025-11-22 20:00 | flat_start_nr | 150.95 | 7 | 534 | 2025-11
2025-11-22 21:00 | flat_start_nr | 151.92 | 7 | 534 | 2025-11
2025-11-22 22:00 | flat_start_nr | 146.94 | 7 | 540 | 2025-11
2025-11-22 23:00 | flat_start_nr | 141.23 | 6 | 546 | 2025-11
2025-11-23 | flat_start_nr | 152.89 | 7 | 534 | 2025-11
2025-11-23 03:00 | flat_start_nr | 157.2 | 7 | 557 | 2025-11
2025-11-23 04:00 | normal_nr | 158.68 | 7 | 543 | 2025-11
2025-11-23 05:00 | flat_start_nr | 156.65 | 7 | 557 | 2025-11
2025-11-23 06:00 | flat_start_nr | 156.59 | 8 | 554 | 2025-11
2025-11-23 07:00 | flat_start_nr | 152.99 | 8 | 533 | 2025-11
2025-11-23 12:00 | flat_start_nr | 153.17 | 7 | 535 | 2025-11
2025-11-23 13:00 | flat_start_nr | 135.23 | 5 | 536 | 2025-11
2025-11-23 14:00 | flat_start_nr | 133.45 | 5 | 526 | 2025-11
2025-11-23 15:00 | flat_start_nr | 141.67 | 5 | 531 | 2025-11
2025-11-23 16:00 | flat_start_nr | 132.13 | 5 | 536 | 2025-11
2025-11-23 17:00 | flat_start_nr | 120.09 | 4 | 544 | 2025-11
2025-11-23 18:00 | flat_start_nr | 127.07 | 4 | 549 | 2025-11
2025-11-23 19:00 | flat_start_nr | 118.68 | 4 | 546 | 2025-11
2025-11-23 20:00 | flat_start_nr | 116.53 | 3 | 548 | 2025-11
2025-11-23 21:00 | flat_start_nr | 116.43 | 3 | 550 | 2025-11
2025-11-23 22:00 | flat_start_nr | 116.89 | 4 | 548 | 2025-11
2025-11-23 23:00 | flat_start_nr | 123.98 | 4 | 552 | 2025-11
2025-11-24 | flat_start_nr | 141.45 | 4 | 552 | 2025-11
2025-11-24 01:00 | flat_start_nr | 156.08 | 6 | 552 | 2025-11
2025-11-24 02:00 | flat_start_nr | 155.15 | 6 | 555 | 2025-11
2025-11-24 03:00 | flat_start_nr | 145.96 | 6 | 543 | 2025-11
2025-11-24 04:00 | flat_start_nr | 133.9 | 5 | 548 | 2025-11
2025-11-24 05:00 | flat_start_nr | 140.38 | 5 | 547 | 2025-11
2025-11-24 06:00 | flat_start_nr | 134.95 | 5 | 543 | 2025-11
2025-11-24 07:00 | flat_start_nr | 132.56 | 5 | 542 | 2025-11
2025-11-24 08:00 | flat_start_nr | 121.02 | 4 | 542 | 2025-11
2025-11-24 09:00 | flat_start_nr | 133.24 | 6 | 544 | 2025-11
2025-11-24 10:00 | flat_start_nr | 150.29 | 9 | 521 | 2025-11
2025-11-24 11:00 | flat_start_nr | 152.4 | 8 | 528 | 2025-11
2025-11-24 12:00 | flat_start_nr | 137.85 | 6 | 541 | 2025-11
2025-11-24 13:00 | flat_start_nr | 131.85 | 6 | 532 | 2025-11
2025-11-24 14:00 | flat_start_nr | 126.21 | 5 | 524 | 2025-11
2025-11-24 15:00 | flat_start_nr | 125.5 | 5 | 524 | 2025-11
2025-11-24 16:00 | flat_start_nr | 123.4 | 5 | 546 | 2025-11
2025-11-24 17:00 | flat_start_nr | 116.56 | 4 | 538 | 2025-11
2025-11-24 18:00 | flat_start_nr | 130.79 | 4 | 550 | 2025-11
2025-11-24 19:00 | flat_start_nr | 134.43 | 3 | 551 | 2025-11
2025-11-24 20:00 | flat_start_nr | 135.84 | 3 | 548 | 2025-11
2025-11-24 21:00 | flat_start_nr | 139.74 | 3 | 548 | 2025-11
2025-11-24 22:00 | flat_start_nr | 136.04 | 3 | 546 | 2025-11
2025-11-24 23:00 | flat_start_nr | 136.06 | 3 | 551 | 2025-11
2025-11-25 | flat_start_nr | 134.06 | 3 | 550 | 2025-11
2025-11-25 01:00 | flat_start_nr | 130.6 | 3 | 545 | 2025-11
2025-11-25 02:00 | flat_start_nr | 139.18 | 3 | 544 | 2025-11
2025-11-25 03:00 | flat_start_nr | 140.71 | 3 | 547 | 2025-11
2025-11-25 04:00 | flat_start_nr | 146.83 | 4 | 535 | 2025-11
2025-11-25 05:00 | flat_start_nr | 146.36 | 4 | 535 | 2025-11
2025-11-25 06:00 | flat_start_nr | 141.55 | 3 | 548 | 2025-11
2025-11-25 07:00 | flat_start_nr | 133.5 | 3 | 549 | 2025-11
2025-11-25 08:00 | flat_start_nr | 144.73 | 3 | 540 | 2025-11
2025-11-25 16:00 | flat_start_nr | 141.79 | 4 | 551 | 2025-11
2025-11-25 17:00 | flat_start_nr | 133.82 | 4 | 537 | 2025-11
2025-11-25 18:00 | flat_start_nr | 139.14 | 4 | 530 | 2025-11
2025-11-25 19:00 | flat_start_nr | 139.87 | 4 | 530 | 2025-11
2025-11-25 20:00 | flat_start_nr | 138.12 | 4 | 541 | 2025-11
2025-11-25 21:00 | flat_start_nr | 138.53 | 4 | 539 | 2025-11
2025-11-25 22:00 | flat_start_nr | 133.26 | 4 | 539 | 2025-11
2025-11-25 23:00 | flat_start_nr | 139.4 | 4 | 541 | 2025-11
2025-11-26 | flat_start_nr | 139.92 | 4 | 547 | 2025-11
2025-11-26 01:00 | flat_start_nr | 142.37 | 4 | 541 | 2025-11
2025-11-26 02:00 | flat_start_nr | 142.36 | 4 | 543 | 2025-11
2025-11-26 03:00 | flat_start_nr | 154.3 | 6 | 522 | 2025-11
2025-11-26 04:00 | flat_start_nr | 145.54 | 5 | 552 | 2025-11
2025-11-26 05:00 | flat_start_nr | 138.45 | 5 | 545 | 2025-11
2025-11-26 06:00 | flat_start_nr | 136.62 | 4 | 548 | 2025-11
2025-11-26 07:00 | flat_start_nr | 120.9 | 2 | 548 | 2025-11
2025-11-26 08:00 | flat_start_nr | 133.06 | 3 | 538 | 2025-11
2025-11-26 09:00 | flat_start_nr | 137.67 | 3 | 542 | 2025-11
2025-11-26 10:00 | flat_start_nr | 145.12 | 3 | 541 | 2025-11
2025-11-26 11:00 | flat_start_nr | 148.07 | 4 | 519 | 2025-11
2025-11-26 12:00 | flat_start_nr | 140.06 | 3 | 539 | 2025-11
2025-11-26 13:00 | flat_start_nr | 151.21 | 5 | 543 | 2025-11
2025-11-26 14:00 | flat_start_nr | 139.83 | 3 | 541 | 2025-11
2025-11-26 15:00 | flat_start_nr | 134.97 | 3 | 539 | 2025-11
2025-11-26 16:00 | flat_start_nr | 125.58 | 3 | 553 | 2025-11
2025-11-26 17:00 | flat_start_nr | 120.1 | 2 | 547 | 2025-11
2025-11-26 18:00 | flat_start_nr | 128.24 | 2 | 545 | 2025-11
2025-11-26 19:00 | flat_start_nr | 127.63 | 2 | 546 | 2025-11
2025-11-26 20:00 | flat_start_nr | 117.54 | 2 | 548 | 2025-11
2025-11-26 21:00 | flat_start_nr | 111.71 | 2 | 542 | 2025-11
2025-11-26 22:00 | flat_start_nr | 118.35 | 2 | 547 | 2025-11
2025-11-26 23:00 | flat_start_nr | 118.64 | 3 | 550 | 2025-11
2025-11-27 | flat_start_nr | 118.69 | 3 | 540 | 2025-11
2025-11-27 01:00 | flat_start_nr | 118.59 | 3 | 544 | 2025-11
2025-11-27 02:00 | flat_start_nr | 118.67 | 3 | 539 | 2025-11
2025-11-27 03:00 | flat_start_nr | 124.14 | 4 | 531 | 2025-11
2025-11-27 04:00 | flat_start_nr | 122.47 | 4 | 531 | 2025-11
2025-11-27 05:00 | flat_start_nr | 119.65 | 4 | 536 | 2025-11
2025-11-27 06:00 | flat_start_nr | 118.98 | 3 | 548 | 2025-11
2025-11-27 07:00 | flat_start_nr | 124.24 | 3 | 542 | 2025-11
2025-11-27 08:00 | flat_start_nr | 138 | 3 | 534 | 2025-11
2025-11-27 09:00 | flat_start_nr | 151.26 | 5 | 522 | 2025-11
2025-11-27 11:00 | flat_start_nr | 152.5 | 7 | 520 | 2025-11
2025-11-27 12:00 | flat_start_nr | 147.35 | 6 | 521 | 2025-11
2025-11-27 13:00 | flat_start_nr | 139.2 | 5 | 528 | 2025-11
2025-11-27 14:00 | flat_start_nr | 130.38 | 5 | 523 | 2025-11
2025-11-27 15:00 | flat_start_nr | 122.75 | 4 | 525 | 2025-11
2025-11-27 16:00 | flat_start_nr | 116.94 | 3 | 542 | 2025-11
2025-11-27 17:00 | flat_start_nr | 123.08 | 4 | 531 | 2025-11
2025-11-27 18:00 | flat_start_nr | 125.98 | 4 | 528 | 2025-11
2025-11-27 19:00 | flat_start_nr | 125.21 | 3 | 529 | 2025-11
2025-11-27 20:00 | flat_start_nr | 123.07 | 3 | 529 | 2025-11
2025-11-27 21:00 | flat_start_nr | 126.96 | 4 | 526 | 2025-11
2025-11-27 22:00 | flat_start_nr | 129.68 | 5 | 525 | 2025-11
2025-11-27 23:00 | flat_start_nr | 136.81 | 5 | 529 | 2025-11
2025-11-28 | flat_start_nr | 143.36 | 5 | 529 | 2025-11
2025-11-28 01:00 | flat_start_nr | 138.34 | 5 | 529 | 2025-11
2025-11-28 02:00 | flat_start_nr | 139.11 | 5 | 525 | 2025-11
2025-11-28 03:00 | flat_start_nr | 141.75 | 4 | 530 | 2025-11
2025-11-28 04:00 | flat_start_nr | 140.24 | 4 | 523 | 2025-11
2025-11-28 05:00 | flat_start_nr | 136.57 | 4 | 523 | 2025-11
2025-11-28 06:00 | flat_start_nr | 135.76 | 4 | 526 | 2025-11
2025-11-28 07:00 | flat_start_nr | 127.83 | 3 | 527 | 2025-11
2025-11-28 08:00 | flat_start_nr | 144.66 | 5 | 529 | 2025-11
2025-11-28 09:00 | flat_start_nr | 154.01 | 7 | 530 | 2025-11
2025-11-28 11:00 | flat_start_nr | 144.7 | 5 | 529 | 2025-11
2025-11-28 12:00 | flat_start_nr | 150.82 | 6 | 519 | 2025-11
2025-11-28 13:00 | flat_start_nr | 151.41 | 7 | 512 | 2025-11
2025-11-28 14:00 | flat_start_nr | 149.48 | 6 | 513 | 2025-11
2025-11-28 15:00 | flat_start_nr | 139.04 | 5 | 530 | 2025-11
2025-11-28 16:00 | flat_start_nr | 138.33 | 5 | 542 | 2025-11
2025-11-28 17:00 | flat_start_nr | 124.51 | 4 | 539 | 2025-11
2025-11-28 18:00 | flat_start_nr | 119.45 | 3 | 540 | 2025-11
2025-11-28 19:00 | flat_start_nr | 114.05 | 2 | 531 | 2025-11
2025-11-28 20:00 | flat_start_nr | 115.13 | 3 | 536 | 2025-11
2025-11-28 21:00 | flat_start_nr | 119.12 | 4 | 539 | 2025-11
2025-11-28 22:00 | flat_start_nr | 117.46 | 4 | 540 | 2025-11
2025-11-28 23:00 | flat_start_nr | 118.98 | 4 | 536 | 2025-11
2025-11-29 | flat_start_nr | 121.64 | 4 | 531 | 2025-11
2025-11-29 01:00 | flat_start_nr | 124.12 | 4 | 528 | 2025-11
2025-11-29 02:00 | flat_start_nr | 133.92 | 4 | 539 | 2025-11
2025-11-29 03:00 | flat_start_nr | 136.95 | 4 | 541 | 2025-11
2025-11-29 04:00 | flat_start_nr | 133.61 | 4 | 543 | 2025-11
2025-11-29 05:00 | flat_start_nr | 133.35 | 4 | 534 | 2025-11
2025-11-29 06:00 | flat_start_nr | 138.87 | 4 | 539 | 2025-11
2025-11-29 07:00 | flat_start_nr | 140.05 | 4 | 543 | 2025-11
2025-11-29 08:00 | flat_start_nr | 142.5 | 4 | 538 | 2025-11
2025-11-29 09:00 | flat_start_nr | 138.89 | 4 | 528 | 2025-11
2025-11-29 10:00 | flat_start_nr | 140.92 | 4 | 536 | 2025-11
2025-11-29 11:00 | flat_start_nr | 145.95 | 5 | 538 | 2025-11
2025-11-29 12:00 | flat_start_nr | 150.18 | 5 | 525 | 2025-11
2025-11-29 13:00 | flat_start_nr | 146.62 | 5 | 532 | 2025-11
2025-11-29 14:00 | flat_start_nr | 152.9 | 7 | 520 | 2025-11
2025-11-29 15:00 | flat_start_nr | 139.44 | 5 | 540 | 2025-11
2025-11-29 16:00 | flat_start_nr | 118.31 | 4 | 527 | 2025-11
2025-11-29 17:00 | flat_start_nr | 113.29 | 3 | 529 | 2025-11
2025-11-29 18:00 | flat_start_nr | 121.28 | 4 | 541 | 2025-11
2025-11-29 19:00 | flat_start_nr | 121.65 | 4 | 540 | 2025-11
2025-11-29 20:00 | flat_start_nr | 122.4 | 4 | 536 | 2025-11
2025-11-29 21:00 | flat_start_nr | 135.14 | 5 | 533 | 2025-11
2025-11-29 22:00 | flat_start_nr | 120.41 | 4 | 530 | 2025-11
2025-11-29 23:00 | flat_start_nr | 120.17 | 4 | 529 | 2025-11
2025-11-30 | flat_start_nr | 125.85 | 4 | 533 | 2025-11
2025-11-30 01:00 | flat_start_nr | 119.05 | 4 | 538 | 2025-11
2025-11-30 02:00 | flat_start_nr | 119.64 | 5 | 538 | 2025-11
2025-11-30 03:00 | flat_start_nr | 121.36 | 5 | 539 | 2025-11
2025-11-30 04:00 | flat_start_nr | 118.56 | 5 | 544 | 2025-11
2025-11-30 05:00 | flat_start_nr | 126.44 | 5 | 543 | 2025-11
2025-11-30 06:00 | flat_start_nr | 120.35 | 5 | 542 | 2025-11
2025-11-30 07:00 | flat_start_nr | 123.67 | 5 | 544 | 2025-11
2025-11-30 08:00 | flat_start_nr | 131.93 | 6 | 547 | 2025-11
2025-11-30 09:00 | flat_start_nr | 138.67 | 6 | 540 | 2025-11
2025-11-30 10:00 | flat_start_nr | 149.34 | 7 | 529 | 2025-11
2025-11-30 11:00 | flat_start_nr | 146.47 | 7 | 536 | 2025-11
2025-11-30 12:00 | flat_start_nr | 141.19 | 7 | 544 | 2025-11
2025-11-30 13:00 | flat_start_nr | 147.65 | 7 | 530 | 2025-11
2025-11-30 14:00 | flat_start_nr | 147.71 | 7 | 532 | 2025-11
2025-11-30 15:00 | flat_start_nr | 140.51 | 6 | 540 | 2025-11
2025-11-30 16:00 | flat_start_nr | 120.3 | 5 | 531 | 2025-11
2025-11-30 17:00 | flat_start_nr | 116.14 | 3 | 540 | 2025-11
2025-11-30 18:00 | flat_start_nr | 119.97 | 4 | 537 | 2025-11
2025-11-30 19:00 | flat_start_nr | 129.32 | 4 | 542 | 2025-11
2025-11-30 20:00 | flat_start_nr | 131.59 | 5 | 548 | 2025-11
2025-11-30 21:00 | flat_start_nr | 123.62 | 4 | 543 | 2025-11
2025-11-30 22:00 | flat_start_nr | 126.95 | 4 | 544 | 2025-11
2025-11-30 23:00 | flat_start_nr | 127.09 | 4 | 541 | 2025-11
2025-12-01 | flat_start_nr | 137.62 | 5 | 545 | 2025-12
2025-12-01 01:00 | flat_start_nr | 141.75 | 4 | 541 | 2025-12
2025-12-01 02:00 | flat_start_nr | 141.23 | 4 | 545 | 2025-12
2025-12-01 03:00 | flat_start_nr | 138.43 | 5 | 543 | 2025-12
2025-12-01 04:00 | flat_start_nr | 134.6 | 5 | 541 | 2025-12
2025-12-01 05:00 | flat_start_nr | 131.69 | 5 | 537 | 2025-12
2025-12-01 06:00 | flat_start_nr | 120.95 | 4 | 532 | 2025-12
2025-12-01 07:00 | flat_start_nr | 120.38 | 4 | 530 | 2025-12
2025-12-01 08:00 | flat_start_nr | 144.11 | 5 | 532 | 2025-12
2025-12-01 09:00 | flat_start_nr | 149.88 | 5 | 525 | 2025-12
2025-12-01 10:00 | flat_start_nr | 155.7 | 6 | 533 | 2025-12
2025-12-01 11:00 | flat_start_nr | 151.57 | 7 | 524 | 2025-12
2025-12-01 12:00 | flat_start_nr | 153.46 | 7 | 524 | 2025-12
2025-12-01 13:00 | flat_start_nr | 151.81 | 7 | 525 | 2025-12
2025-12-01 14:00 | flat_start_nr | 153.26 | 7 | 530 | 2025-12
2025-12-01 15:00 | flat_start_nr | 154.24 | 7 | 547 | 2025-12
2025-12-01 16:00 | flat_start_nr | 143.19 | 5 | 546 | 2025-12
2025-12-01 17:00 | flat_start_nr | 133.69 | 5 | 538 | 2025-12
2025-12-01 18:00 | flat_start_nr | 136.01 | 6 | 546 | 2025-12
2025-12-01 19:00 | flat_start_nr | 141.64 | 6 | 554 | 2025-12
2025-12-01 20:00 | flat_start_nr | 149.01 | 6 | 535 | 2025-12
2025-12-01 21:00 | flat_start_nr | 152.62 | 6 | 532 | 2025-12
2025-12-02 07:00 | flat_start_nr | 142.9 | 5 | 546 | 2025-12
2025-12-02 08:00 | flat_start_nr | 152.88 | 6 | 520 | 2025-12
2025-12-02 09:00 | flat_start_nr | 154.63 | 6 | 543 | 2025-12
2025-12-02 10:00 | flat_start_nr | 146.89 | 6 | 540 | 2025-12
2025-12-02 11:00 | flat_start_nr | 139.69 | 5 | 547 | 2025-12
2025-12-02 12:00 | flat_start_nr | 138.87 | 4 | 543 | 2025-12
2025-12-02 13:00 | flat_start_nr | 139.62 | 4 | 542 | 2025-12
2025-12-02 14:00 | flat_start_nr | 137.24 | 4 | 540 | 2025-12
2025-12-02 15:00 | flat_start_nr | 133.85 | 4 | 537 | 2025-12
2025-12-02 16:00 | flat_start_nr | 137.47 | 5 | 538 | 2025-12
2025-12-02 17:00 | flat_start_nr | 123.73 | 4 | 535 | 2025-12
2025-12-02 18:00 | flat_start_nr | 126.13 | 3 | 534 | 2025-12
2025-12-02 19:00 | flat_start_nr | 120.91 | 4 | 535 | 2025-12
2025-12-02 20:00 | flat_start_nr | 121.53 | 2 | 548 | 2025-12
2025-12-02 21:00 | flat_start_nr | 124.45 | 2 | 548 | 2025-12
2025-12-02 22:00 | flat_start_nr | 146.81 | 4 | 547 | 2025-12
2025-12-02 23:00 | flat_start_nr | 140.76 | 4 | 551 | 2025-12
2025-12-03 | flat_start_nr | 146.24 | 6 | 545 | 2025-12
2025-12-03 01:00 | flat_start_nr | 141.36 | 5 | 547 | 2025-12
2025-12-03 02:00 | flat_start_nr | 139.88 | 5 | 543 | 2025-12
2025-12-03 03:00 | flat_start_nr | 138.81 | 5 | 548 | 2025-12
2025-12-03 04:00 | flat_start_nr | 137.96 | 5 | 548 | 2025-12
2025-12-03 05:00 | flat_start_nr | 144.13 | 5 | 551 | 2025-12
2025-12-03 06:00 | flat_start_nr | 152.81 | 7 | 533 | 2025-12
2025-12-03 07:00 | flat_start_nr | 148.72 | 5 | 532 | 2025-12
2025-12-03 12:00 | flat_start_nr | 151.55 | 7 | 540 | 2025-12
2025-12-03 15:00 | flat_start_nr | 153.83 | 9 | 539 | 2025-12
2025-12-03 16:00 | flat_start_nr | 137.93 | 7 | 549 | 2025-12
2025-12-03 17:00 | flat_start_nr | 133.31 | 7 | 558 | 2025-12
2025-12-03 18:00 | flat_start_nr | 139.23 | 7 | 565 | 2025-12
2025-12-03 19:00 | flat_start_nr | 145.61 | 7 | 569 | 2025-12
2025-12-04 06:00 | flat_start_nr | 153.31 | 8 | 535 | 2025-12
2025-12-04 07:00 | flat_start_nr | 139.64 | 6 | 555 | 2025-12
2025-12-04 08:00 | flat_start_nr | 131.67 | 5 | 532 | 2025-12
2025-12-04 09:00 | flat_start_nr | 136.39 | 4 | 530 | 2025-12
2025-12-04 10:00 | flat_start_nr | 146.53 | 6 | 525 | 2025-12
2025-12-04 11:00 | flat_start_nr | 147.36 | 6 | 528 | 2025-12
2025-12-04 12:00 | flat_start_nr | 144.73 | 5 | 535 | 2025-12
2025-12-04 13:00 | flat_start_nr | 145.18 | 5 | 531 | 2025-12
2025-12-04 14:00 | flat_start_nr | 146.63 | 6 | 529 | 2025-12
2025-12-04 15:00 | flat_start_nr | 143.69 | 4 | 542 | 2025-12
2025-12-04 16:00 | flat_start_nr | 127.69 | 4 | 537 | 2025-12
2025-12-04 17:00 | flat_start_nr | 124.76 | 4 | 534 | 2025-12
2025-12-04 18:00 | flat_start_nr | 127.64 | 3 | 535 | 2025-12
2025-12-04 19:00 | flat_start_nr | 118.44 | 3 | 536 | 2025-12
2025-12-04 20:00 | flat_start_nr | 122.03 | 4 | 535 | 2025-12
2025-12-04 21:00 | flat_start_nr | 133.05 | 5 | 541 | 2025-12
2025-12-04 22:00 | flat_start_nr | 159.07 | 8 | 535 | 2025-12
2025-12-05 | flat_start_nr | 157.8 | 7 | 553 | 2025-12
2025-12-05 01:00 | normal_nr | 161.42 | 7 | 554 | 2025-12
2025-12-05 03:00 | flat_start_nr | 144.67 | 4 | 540 | 2025-12
2025-12-05 04:00 | flat_start_nr | 156.19 | 6 | 553 | 2025-12
2025-12-05 05:00 | flat_start_nr | 155.68 | 6 | 555 | 2025-12
2025-12-05 06:00 | flat_start_nr | 143.57 | 4 | 551 | 2025-12
2025-12-05 07:00 | flat_start_nr | 131.35 | 3 | 549 | 2025-12
2025-12-05 08:00 | flat_start_nr | 136.7 | 3 | 552 | 2025-12
2025-12-05 14:00 | flat_start_nr | 152.43 | 6 | 529 | 2025-12
2025-12-05 16:00 | flat_start_nr | 124.38 | 5 | 529 | 2025-12
2025-12-05 17:00 | flat_start_nr | 126.1 | 5 | 538 | 2025-12
2025-12-05 18:00 | flat_start_nr | 129.54 | 5 | 537 | 2025-12
2025-12-05 19:00 | flat_start_nr | 119.62 | 5 | 544 | 2025-12
2025-12-05 20:00 | flat_start_nr | 116.73 | 4 | 534 | 2025-12
2025-12-05 21:00 | flat_start_nr | 116.12 | 4 | 537 | 2025-12
2025-12-05 22:00 | flat_start_nr | 121.7 | 5 | 533 | 2025-12
2025-12-05 23:00 | flat_start_nr | 121.65 | 5 | 536 | 2025-12
2025-12-06 | flat_start_nr | 130.75 | 5 | 540 | 2025-12
2025-12-06 01:00 | flat_start_nr | 134.06 | 5 | 541 | 2025-12
2025-12-06 02:00 | flat_start_nr | 132.54 | 5 | 537 | 2025-12
2025-12-06 03:00 | flat_start_nr | 128.1 | 4 | 538 | 2025-12
2025-12-06 04:00 | flat_start_nr | 130.78 | 5 | 536 | 2025-12
2025-12-06 05:00 | flat_start_nr | 136.83 | 5 | 541 | 2025-12
2025-12-06 06:00 | flat_start_nr | 119.54 | 4 | 538 | 2025-12
2025-12-06 07:00 | flat_start_nr | 116.26 | 3 | 545 | 2025-12
2025-12-06 08:00 | flat_start_nr | 119.23 | 4 | 538 | 2025-12
2025-12-06 09:00 | flat_start_nr | 123.91 | 4 | 536 | 2025-12
2025-12-06 10:00 | flat_start_nr | 126.64 | 4 | 539 | 2025-12
2025-12-06 11:00 | flat_start_nr | 125.34 | 4 | 535 | 2025-12
2025-12-06 12:00 | flat_start_nr | 130.03 | 5 | 534 | 2025-12
2025-12-06 13:00 | flat_start_nr | 137.52 | 5 | 537 | 2025-12
2025-12-06 14:00 | flat_start_nr | 136.97 | 5 | 533 | 2025-12
2025-12-06 15:00 | flat_start_nr | 148.97 | 7 | 524 | 2025-12
2025-12-06 16:00 | flat_start_nr | 141.9 | 5 | 547 | 2025-12
2025-12-06 17:00 | flat_start_nr | 135.4 | 5 | 543 | 2025-12
2025-12-06 18:00 | flat_start_nr | 143.81 | 5 | 554 | 2025-12
2025-12-06 19:00 | flat_start_nr | 130.54 | 6 | 549 | 2025-12
2025-12-06 20:00 | flat_start_nr | 126.93 | 4 | 549 | 2025-12
2025-12-06 21:00 | flat_start_nr | 133.61 | 5 | 549 | 2025-12
2025-12-06 22:00 | flat_start_nr | 133.44 | 6 | 547 | 2025-12
2025-12-06 23:00 | flat_start_nr | 133.16 | 5 | 547 | 2025-12
2025-12-07 | flat_start_nr | 144.01 | 6 | 545 | 2025-12
2025-12-07 01:00 | flat_start_nr | 149.23 | 6 | 534 | 2025-12
2025-12-07 02:00 | flat_start_nr | 140.15 | 4 | 549 | 2025-12
2025-12-07 03:00 | flat_start_nr | 129.34 | 4 | 544 | 2025-12
2025-12-07 04:00 | flat_start_nr | 132.47 | 5 | 542 | 2025-12
2025-12-07 05:00 | flat_start_nr | 133.07 | 5 | 541 | 2025-12
2025-12-07 06:00 | flat_start_nr | 142.17 | 4 | 542 | 2025-12
2025-12-07 07:00 | flat_start_nr | 152.2 | 6 | 521 | 2025-12
2025-12-07 09:00 | flat_start_nr | 133.4 | 5 | 532 | 2025-12
2025-12-07 10:00 | flat_start_nr | 129.39 | 5 | 532 | 2025-12
2025-12-07 11:00 | flat_start_nr | 136.29 | 5 | 531 | 2025-12
2025-12-07 12:00 | flat_start_nr | 133.51 | 5 | 530 | 2025-12
2025-12-07 13:00 | flat_start_nr | 137.13 | 5 | 534 | 2025-12
2025-12-07 14:00 | flat_start_nr | 142.23 | 5 | 541 | 2025-12
2025-12-07 15:00 | flat_start_nr | 148.47 | 5 | 528 | 2025-12
2025-12-07 16:00 | flat_start_nr | 136.65 | 5 | 533 | 2025-12
2025-12-07 17:00 | flat_start_nr | 135.2 | 5 | 539 | 2025-12
2025-12-07 18:00 | flat_start_nr | 141.87 | 6 | 539 | 2025-12
2025-12-07 19:00 | flat_start_nr | 149.65 | 7 | 538 | 2025-12
2025-12-07 20:00 | flat_start_nr | 141.93 | 6 | 557 | 2025-12
2025-12-07 21:00 | flat_start_nr | 151.76 | 6 | 543 | 2025-12
2025-12-08 04:00 | flat_start_nr | 154.45 | 8 | 531 | 2025-12
2025-12-08 05:00 | flat_start_nr | 141.54 | 6 | 553 | 2025-12
2025-12-08 06:00 | flat_start_nr | 132.07 | 5 | 539 | 2025-12
2025-12-08 07:00 | flat_start_nr | 128.99 | 4 | 540 | 2025-12
2025-12-08 08:00 | flat_start_nr | 140.95 | 4 | 535 | 2025-12
2025-12-08 14:00 | flat_start_nr | 151.56 | 8 | 524 | 2025-12
2025-12-08 15:00 | flat_start_nr | 150.09 | 7 | 524 | 2025-12
2025-12-08 16:00 | flat_start_nr | 140.04 | 6 | 539 | 2025-12
2025-12-08 17:00 | flat_start_nr | 135.44 | 4 | 538 | 2025-12
2025-12-08 18:00 | flat_start_nr | 135.17 | 5 | 536 | 2025-12
2025-12-08 19:00 | flat_start_nr | 135 | 6 | 540 | 2025-12
2025-12-08 20:00 | flat_start_nr | 138.52 | 6 | 554 | 2025-12
2025-12-08 21:00 | flat_start_nr | 135.18 | 6 | 540 | 2025-12
2025-12-08 22:00 | flat_start_nr | 140.12 | 6 | 551 | 2025-12
2025-12-08 23:00 | flat_start_nr | 142.84 | 6 | 550 | 2025-12
2025-12-09 | flat_start_nr | 152.09 | 7 | 533 | 2025-12
2025-12-09 06:00 | flat_start_nr | 139.79 | 5 | 553 | 2025-12
2025-12-09 07:00 | flat_start_nr | 130.54 | 5 | 547 | 2025-12
2025-12-09 08:00 | flat_start_nr | 136.57 | 5 | 546 | 2025-12
2025-12-09 09:00 | flat_start_nr | 145.53 | 5 | 540 | 2025-12
2025-12-09 16:00 | flat_start_nr | 144.8 | 5 | 536 | 2025-12
2025-12-09 17:00 | flat_start_nr | 129.15 | 4 | 544 | 2025-12
2025-12-09 18:00 | flat_start_nr | 149.75 | 4 | 552 | 2025-12
2025-12-09 22:00 | flat_start_nr | 152.55 | 6 | 519 | 2025-12
2025-12-09 23:00 | flat_start_nr | 140.27 | 5 | 540 | 2025-12
2025-12-10 | flat_start_nr | 145.51 | 6 | 537 | 2025-12
2025-12-10 01:00 | flat_start_nr | 153.85 | 6 | 510 | 2025-12
2025-12-10 02:00 | flat_start_nr | 152.98 | 7 | 520 | 2025-12
2025-12-10 03:00 | normal_nr | 160.85 | 7 | 555 | 2025-12
2025-12-10 04:00 | flat_start_nr | 158.65 | 7 | 543 | 2025-12
2025-12-10 05:00 | normal_nr | 161.03 | 7 | 559 | 2025-12
2025-12-10 06:00 | flat_start_nr | 159.21 | 6 | 550 | 2025-12
2025-12-10 07:00 | flat_start_nr | 151.54 | 5 | 533 | 2025-12
2025-12-10 08:00 | flat_start_nr | 144.26 | 5 | 541 | 2025-12
2025-12-10 09:00 | flat_start_nr | 149.47 | 5 | 529 | 2025-12
2025-12-10 10:00 | flat_start_nr | 151.62 | 6 | 525 | 2025-12
2025-12-10 11:00 | flat_start_nr | 146.68 | 5 | 531 | 2025-12
2025-12-10 12:00 | flat_start_nr | 143.41 | 4 | 544 | 2025-12
2025-12-10 13:00 | flat_start_nr | 145.46 | 5 | 530 | 2025-12
2025-12-10 14:00 | flat_start_nr | 145.03 | 4 | 536 | 2025-12
2025-12-10 15:00 | flat_start_nr | 134.38 | 5 | 531 | 2025-12
2025-12-10 16:00 | flat_start_nr | 116.67 | 3 | 539 | 2025-12
2025-12-10 17:00 | flat_start_nr | 116.61 | 2 | 534 | 2025-12
2025-12-10 18:00 | flat_start_nr | 117.16 | 3 | 536 | 2025-12
2025-12-10 19:00 | flat_start_nr | 124.29 | 4 | 544 | 2025-12
2025-12-10 20:00 | flat_start_nr | 117.18 | 3 | 549 | 2025-12
2025-12-10 21:00 | flat_start_nr | 123.94 | 4 | 548 | 2025-12
2025-12-10 22:00 | flat_start_nr | 121.46 | 4 | 544 | 2025-12
2025-12-10 23:00 | flat_start_nr | 123.97 | 4 | 551 | 2025-12
2025-12-11 | flat_start_nr | 118.48 | 4 | 540 | 2025-12
2025-12-11 01:00 | flat_start_nr | 118.42 | 4 | 540 | 2025-12
2025-12-11 02:00 | flat_start_nr | 117.82 | 4 | 541 | 2025-12
2025-12-11 03:00 | flat_start_nr | 129.23 | 4 | 544 | 2025-12
2025-12-11 04:00 | flat_start_nr | 139.99 | 5 | 552 | 2025-12
2025-12-11 05:00 | flat_start_nr | 140.12 | 4 | 554 | 2025-12
2025-12-11 06:00 | flat_start_nr | 134.24 | 4 | 546 | 2025-12
2025-12-11 07:00 | flat_start_nr | 132.31 | 4 | 545 | 2025-12
2025-12-11 08:00 | flat_start_nr | 135.45 | 4 | 551 | 2025-12
2025-12-11 09:00 | flat_start_nr | 140.62 | 4 | 543 | 2025-12
2025-12-11 10:00 | flat_start_nr | 129.87 | 4 | 540 | 2025-12
2025-12-11 11:00 | flat_start_nr | 125.65 | 3 | 540 | 2025-12
2025-12-11 12:00 | flat_start_nr | 139.02 | 4 | 541 | 2025-12
2025-12-11 13:00 | flat_start_nr | 145.89 | 5 | 547 | 2025-12
2025-12-11 14:00 | flat_start_nr | 147.58 | 5 | 532 | 2025-12
2025-12-11 15:00 | flat_start_nr | 146.66 | 5 | 530 | 2025-12
2025-12-11 16:00 | flat_start_nr | 125.19 | 4 | 556 | 2025-12
2025-12-11 17:00 | flat_start_nr | 117.14 | 4 | 546 | 2025-12
2025-12-11 18:00 | flat_start_nr | 124.11 | 4 | 552 | 2025-12
2025-12-11 19:00 | flat_start_nr | 119.91 | 4 | 549 | 2025-12
2025-12-11 20:00 | flat_start_nr | 116.16 | 3 | 539 | 2025-12
2025-12-11 21:00 | flat_start_nr | 115.94 | 3 | 542 | 2025-12
2025-12-11 22:00 | flat_start_nr | 115.9 | 3 | 539 | 2025-12
2025-12-11 23:00 | flat_start_nr | 115.76 | 3 | 536 | 2025-12
2025-12-12 | flat_start_nr | 115.96 | 3 | 535 | 2025-12
2025-12-12 01:00 | flat_start_nr | 115.83 | 3 | 536 | 2025-12
2025-12-12 02:00 | flat_start_nr | 115.97 | 3 | 538 | 2025-12
2025-12-12 03:00 | flat_start_nr | 116.15 | 3 | 532 | 2025-12
2025-12-12 04:00 | flat_start_nr | 115.86 | 3 | 534 | 2025-12
2025-12-12 05:00 | flat_start_nr | 120.24 | 4 | 529 | 2025-12
2025-12-12 06:00 | flat_start_nr | 132.57 | 3 | 536 | 2025-12
2025-12-12 07:00 | flat_start_nr | 125.78 | 2 | 534 | 2025-12
2025-12-12 08:00 | flat_start_nr | 129.46 | 3 | 531 | 2025-12
2025-12-12 09:00 | flat_start_nr | 135.2 | 3 | 529 | 2025-12
2025-12-12 10:00 | flat_start_nr | 132.24 | 4 | 526 | 2025-12
2025-12-12 11:00 | flat_start_nr | 133.22 | 4 | 524 | 2025-12
2025-12-12 12:00 | flat_start_nr | 133.58 | 4 | 523 | 2025-12
2025-12-12 13:00 | flat_start_nr | 135.22 | 5 | 521 | 2025-12
2025-12-12 14:00 | flat_start_nr | 137.14 | 4 | 527 | 2025-12
2025-12-12 15:00 | flat_start_nr | 133.6 | 4 | 529 | 2025-12
2025-12-12 16:00 | flat_start_nr | 118.31 | 5 | 531 | 2025-12
2025-12-12 17:00 | flat_start_nr | 116.63 | 4 | 525 | 2025-12
2025-12-12 18:00 | flat_start_nr | 116.84 | 4 | 525 | 2025-12
2025-12-12 19:00 | flat_start_nr | 117.27 | 4 | 529 | 2025-12
2025-12-12 20:00 | flat_start_nr | 117.27 | 3 | 529 | 2025-12
2025-12-12 21:00 | flat_start_nr | 117.39 | 3 | 530 | 2025-12
2025-12-12 22:00 | flat_start_nr | 117.6 | 3 | 530 | 2025-12
2025-12-12 23:00 | flat_start_nr | 117.49 | 3 | 534 | 2025-12
2025-12-13 | flat_start_nr | 117.46 | 3 | 532 | 2025-12
2025-12-13 01:00 | flat_start_nr | 117.15 | 2 | 531 | 2025-12
2025-12-13 02:00 | flat_start_nr | 117.41 | 3 | 532 | 2025-12
2025-12-13 03:00 | flat_start_nr | 117.81 | 4 | 530 | 2025-12
2025-12-13 04:00 | flat_start_nr | 117.43 | 2 | 532 | 2025-12
2025-12-13 05:00 | flat_start_nr | 117.29 | 2 | 532 | 2025-12
2025-12-13 06:00 | flat_start_nr | 117.43 | 2 | 534 | 2025-12
2025-12-13 07:00 | flat_start_nr | 117.19 | 2 | 530 | 2025-12
2025-12-13 08:00 | flat_start_nr | 117.02 | 3 | 528 | 2025-12
2025-12-13 09:00 | flat_start_nr | 121.05 | 4 | 527 | 2025-12
2025-12-13 10:00 | flat_start_nr | 124.99 | 4 | 519 | 2025-12
2025-12-13 11:00 | flat_start_nr | 132.4 | 5 | 539 | 2025-12
2025-12-13 12:00 | flat_start_nr | 126.09 | 4 | 533 | 2025-12
2025-12-13 13:00 | flat_start_nr | 127.87 | 4 | 534 | 2025-12
2025-12-13 14:00 | flat_start_nr | 136 | 6 | 535 | 2025-12
2025-12-13 15:00 | flat_start_nr | 141.72 | 5 | 543 | 2025-12
2025-12-13 16:00 | flat_start_nr | 133.83 | 5 | 542 | 2025-12
2025-12-13 17:00 | flat_start_nr | 133.79 | 4 | 539 | 2025-12
2025-12-13 18:00 | flat_start_nr | 135.15 | 4 | 540 | 2025-12
2025-12-13 19:00 | flat_start_nr | 136.45 | 6 | 540 | 2025-12
2025-12-13 20:00 | flat_start_nr | 140.13 | 5 | 552 | 2025-12
2025-12-13 21:00 | flat_start_nr | 157.05 | 8 | 550 | 2025-12
2025-12-13 22:00 | flat_start_nr | 158.13 | 8 | 555 | 2025-12
2025-12-14 17:00 | flat_start_nr | 134.81 | 5 | 539 | 2025-12
2025-12-14 18:00 | flat_start_nr | 141.85 | 5 | 540 | 2025-12
2025-12-14 19:00 | flat_start_nr | 153.93 | 6 | 520 | 2025-12
2025-12-14 20:00 | flat_start_nr | 151.4 | 5 | 529 | 2025-12
2025-12-14 21:00 | flat_start_nr | 154.06 | 6 | 520 | 2025-12
2025-12-15 17:00 | flat_start_nr | 144.52 | 5 | 547 | 2025-12
2025-12-15 18:00 | flat_start_nr | 147.45 | 6 | 542 | 2025-12
2025-12-15 19:00 | normal_nr | 160.65 | 7 | 554 | 2025-12
2025-12-15 20:00 | flat_start_nr | 153.04 | 7 | 536 | 2025-12
2025-12-16 06:00 | flat_start_nr | 154.11 | 6 | 540 | 2025-12
2025-12-16 07:00 | flat_start_nr | 148.41 | 5 | 537 | 2025-12
2025-12-16 16:00 | flat_start_nr | 155.83 | 7 | 554 | 2025-12
2025-12-16 17:00 | flat_start_nr | 142.12 | 5 | 559 | 2025-12
2025-12-16 18:00 | flat_start_nr | 144.74 | 5 | 556 | 2025-12
2025-12-16 19:00 | flat_start_nr | 153.18 | 7 | 535 | 2025-12
2025-12-16 20:00 | flat_start_nr | 153.73 | 6 | 529 | 2025-12
2025-12-16 21:00 | flat_start_nr | 155.18 | 7 | 527 | 2025-12
2025-12-16 22:00 | flat_start_nr | 158.49 | 7 | 538 | 2025-12
2025-12-16 23:00 | flat_start_nr | 156.85 | 7 | 552 | 2025-12
2025-12-17 06:00 | flat_start_nr | 155.52 | 7 | 536 | 2025-12
2025-12-17 07:00 | flat_start_nr | 137.56 | 6 | 548 | 2025-12
2025-12-17 08:00 | flat_start_nr | 137.01 | 6 | 544 | 2025-12
2025-12-17 09:00 | flat_start_nr | 145.59 | 6 | 528 | 2025-12
2025-12-17 16:00 | flat_start_nr | 141.75 | 6 | 547 | 2025-12
2025-12-17 17:00 | flat_start_nr | 132.89 | 6 | 543 | 2025-12
2025-12-17 18:00 | flat_start_nr | 129.97 | 5 | 542 | 2025-12
2025-12-17 19:00 | flat_start_nr | 128.86 | 4 | 546 | 2025-12
2025-12-17 20:00 | flat_start_nr | 125.21 | 4 | 542 | 2025-12
2025-12-17 21:00 | flat_start_nr | 117.22 | 4 | 542 | 2025-12
2025-12-17 22:00 | flat_start_nr | 114.48 | 2 | 539 | 2025-12
2025-12-17 23:00 | flat_start_nr | 120.92 | 3 | 544 | 2025-12
2025-12-18 | flat_start_nr | 120.03 | 3 | 543 | 2025-12
2025-12-18 01:00 | flat_start_nr | 121.38 | 3 | 537 | 2025-12
2025-12-18 02:00 | flat_start_nr | 138.11 | 4 | 544 | 2025-12
2025-12-18 03:00 | flat_start_nr | 145.2 | 4 | 542 | 2025-12
2025-12-18 04:00 | flat_start_nr | 156.25 | 6 | 537 | 2025-12
2025-12-18 06:00 | flat_start_nr | 147.03 | 7 | 547 | 2025-12
2025-12-18 07:00 | flat_start_nr | 134.37 | 5 | 544 | 2025-12
2025-12-18 08:00 | flat_start_nr | 137.04 | 6 | 543 | 2025-12
2025-12-18 09:00 | flat_start_nr | 146.48 | 7 | 541 | 2025-12
2025-12-18 10:00 | flat_start_nr | 156.32 | 6 | 559 | 2025-12
2025-12-18 11:00 | flat_start_nr | 156.78 | 6 | 540 | 2025-12
2025-12-18 13:00 | flat_start_nr | 154.72 | 8 | 556 | 2025-12
2025-12-18 14:00 | flat_start_nr | 145.75 | 7 | 547 | 2025-12
2025-12-18 15:00 | flat_start_nr | 145.76 | 7 | 545 | 2025-12
2025-12-18 16:00 | flat_start_nr | 140.81 | 6 | 544 | 2025-12
2025-12-18 17:00 | flat_start_nr | 136.61 | 5 | 552 | 2025-12
2025-12-18 18:00 | flat_start_nr | 136.79 | 5 | 548 | 2025-12
2025-12-18 19:00 | flat_start_nr | 136.91 | 5 | 550 | 2025-12
2025-12-18 20:00 | flat_start_nr | 136.98 | 5 | 545 | 2025-12
2025-12-18 21:00 | flat_start_nr | 136.94 | 5 | 545 | 2025-12
2025-12-18 22:00 | flat_start_nr | 136.44 | 6 | 544 | 2025-12
2025-12-18 23:00 | flat_start_nr | 132.07 | 5 | 543 | 2025-12
2025-12-19 | flat_start_nr | 138.58 | 6 | 548 | 2025-12
2025-12-19 01:00 | flat_start_nr | 147.52 | 7 | 542 | 2025-12
2025-12-19 03:00 | normal_nr | 161.93 | 8 | 551 | 2025-12
2025-12-19 04:00 | normal_nr | 161.31 | 8 | 548 | 2025-12
2025-12-19 06:00 | flat_start_nr | 147.53 | 7 | 538 | 2025-12
2025-12-19 07:00 | flat_start_nr | 138.84 | 6 | 549 | 2025-12
2025-12-19 08:00 | flat_start_nr | 144.04 | 5 | 542 | 2025-12
2025-12-19 09:00 | flat_start_nr | 140.92 | 5 | 541 | 2025-12
2025-12-19 10:00 | flat_start_nr | 137.96 | 4 | 540 | 2025-12
2025-12-19 11:00 | flat_start_nr | 151.82 | 6 | 533 | 2025-12
2025-12-19 12:00 | flat_start_nr | 156.26 | 6 | 545 | 2025-12
2025-12-19 13:00 | flat_start_nr | 148.86 | 5 | 535 | 2025-12
2025-12-19 14:00 | flat_start_nr | 155.3 | 6 | 539 | 2025-12
2025-12-19 16:00 | flat_start_nr | 138.86 | 4 | 543 | 2025-12
2025-12-19 17:00 | flat_start_nr | 122.42 | 3 | 538 | 2025-12
2025-12-19 18:00 | flat_start_nr | 136.84 | 4 | 543 | 2025-12
2025-12-19 19:00 | flat_start_nr | 137.18 | 4 | 543 | 2025-12
2025-12-19 20:00 | flat_start_nr | 137.31 | 4 | 548 | 2025-12
2025-12-19 21:00 | flat_start_nr | 139.28 | 4 | 550 | 2025-12
2025-12-19 22:00 | flat_start_nr | 144.86 | 4 | 546 | 2025-12
2025-12-19 23:00 | flat_start_nr | 146.37 | 5 | 548 | 2025-12
2025-12-20 | flat_start_nr | 149.96 | 5 | 539 | 2025-12
2025-12-20 01:00 | flat_start_nr | 146.35 | 5 | 541 | 2025-12
2025-12-20 02:00 | flat_start_nr | 141.35 | 4 | 551 | 2025-12
2025-12-20 03:00 | flat_start_nr | 134.23 | 4 | 547 | 2025-12
2025-12-20 04:00 | flat_start_nr | 128.62 | 3 | 542 | 2025-12
2025-12-20 05:00 | flat_start_nr | 120.37 | 3 | 537 | 2025-12
2025-12-20 06:00 | flat_start_nr | 113.76 | 1 | 536 | 2025-12
2025-12-20 07:00 | flat_start_nr | 114.57 | 1 | 541 | 2025-12
2025-12-20 08:00 | flat_start_nr | 132.08 | 3 | 535 | 2025-12
2025-12-20 09:00 | flat_start_nr | 134.08 | 3 | 528 | 2025-12
2025-12-20 10:00 | flat_start_nr | 140.72 | 4 | 532 | 2025-12
2025-12-20 11:00 | flat_start_nr | 143.76 | 4 | 521 | 2025-12
2025-12-20 16:00 | flat_start_nr | 152.9 | 6 | 534 | 2025-12
2025-12-20 17:00 | flat_start_nr | 140.68 | 4 | 537 | 2025-12
2025-12-20 18:00 | flat_start_nr | 141.61 | 5 | 542 | 2025-12
2025-12-20 19:00 | flat_start_nr | 142.43 | 6 | 545 | 2025-12
2025-12-20 20:00 | flat_start_nr | 141.32 | 6 | 546 | 2025-12
2025-12-20 21:00 | flat_start_nr | 137.01 | 6 | 541 | 2025-12
2025-12-20 22:00 | flat_start_nr | 133.42 | 5 | 536 | 2025-12
2025-12-20 23:00 | flat_start_nr | 133.41 | 6 | 538 | 2025-12
2025-12-21 | flat_start_nr | 155.68 | 7 | 539 | 2025-12
2025-12-21 03:00 | flat_start_nr | 149.21 | 7 | 542 | 2025-12
2025-12-21 04:00 | flat_start_nr | 141.33 | 6 | 543 | 2025-12
2025-12-21 05:00 | flat_start_nr | 141.92 | 6 | 542 | 2025-12
2025-12-21 06:00 | flat_start_nr | 141.26 | 6 | 541 | 2025-12
2025-12-21 07:00 | flat_start_nr | 141.29 | 6 | 542 | 2025-12
2025-12-21 08:00 | flat_start_nr | 151.42 | 7 | 519 | 2025-12
2025-12-21 13:00 | flat_start_nr | 136.95 | 4 | 530 | 2025-12
2025-12-21 14:00 | flat_start_nr | 127.5 | 3 | 529 | 2025-12
2025-12-21 15:00 | flat_start_nr | 122.92 | 3 | 527 | 2025-12
2025-12-21 16:00 | flat_start_nr | 126.83 | 2 | 535 | 2025-12
2025-12-21 17:00 | flat_start_nr | 119.37 | 2 | 545 | 2025-12
2025-12-21 18:00 | flat_start_nr | 124.99 | 2 | 549 | 2025-12
2025-12-21 19:00 | flat_start_nr | 123.04 | 2 | 550 | 2025-12
2025-12-21 20:00 | flat_start_nr | 114.32 | 1 | 550 | 2025-12
2025-12-21 21:00 | flat_start_nr | 116.29 | 2 | 546 | 2025-12
2025-12-21 22:00 | flat_start_nr | 107.56 | 1 | 538 | 2025-12
2025-12-21 23:00 | flat_start_nr | 106.75 | 1 | 536 | 2025-12
2025-12-22 | flat_start_nr | 106.86 | 1 | 537 | 2025-12
2025-12-22 01:00 | flat_start_nr | 106.88 | 2 | 535 | 2025-12
2025-12-22 02:00 | flat_start_nr | 112.5 | 2 | 535 | 2025-12
2025-12-22 03:00 | flat_start_nr | 112.74 | 2 | 535 | 2025-12
2025-12-22 04:00 | flat_start_nr | 126.08 | 3 | 534 | 2025-12
2025-12-22 05:00 | flat_start_nr | 128.18 | 3 | 534 | 2025-12
2025-12-22 06:00 | flat_start_nr | 121.47 | 3 | 528 | 2025-12
2025-12-22 07:00 | flat_start_nr | 117.02 | 3 | 529 | 2025-12
2025-12-22 08:00 | flat_start_nr | 118.18 | 3 | 537 | 2025-12
2025-12-22 09:00 | flat_start_nr | 124.55 | 3 | 528 | 2025-12
2025-12-22 10:00 | flat_start_nr | 124.14 | 3 | 529 | 2025-12
2025-12-22 11:00 | flat_start_nr | 128.66 | 3 | 531 | 2025-12
2025-12-22 12:00 | flat_start_nr | 130.46 | 4 | 529 | 2025-12
2025-12-22 13:00 | flat_start_nr | 131.64 | 4 | 526 | 2025-12
2025-12-22 14:00 | flat_start_nr | 137.23 | 4 | 530 | 2025-12
2025-12-22 15:00 | flat_start_nr | 148.23 | 4 | 523 | 2025-12
2025-12-22 16:00 | flat_start_nr | 136.79 | 3 | 544 | 2025-12
2025-12-22 17:00 | flat_start_nr | 128.25 | 2 | 543 | 2025-12
2025-12-22 18:00 | flat_start_nr | 121.43 | 2 | 543 | 2025-12
2025-12-22 19:00 | flat_start_nr | 114.62 | 1 | 542 | 2025-12
2025-12-22 20:00 | flat_start_nr | 123.31 | 2 | 536 | 2025-12
2025-12-22 21:00 | flat_start_nr | 140.35 | 4 | 536 | 2025-12
2025-12-22 22:00 | flat_start_nr | 127.66 | 3 | 537 | 2025-12
2025-12-22 23:00 | flat_start_nr | 138.1 | 4 | 541 | 2025-12
2025-12-23 | flat_start_nr | 143.88 | 5 | 547 | 2025-12
2025-12-23 01:00 | flat_start_nr | 149.56 | 6 | 531 | 2025-12
2025-12-23 02:00 | flat_start_nr | 156.31 | 7 | 521 | 2025-12
2025-12-23 07:00 | flat_start_nr | 155.98 | 7 | 539 | 2025-12
2025-12-23 08:00 | normal_nr | 157.04 | 8 | 553 | 2025-12
2025-12-23 14:00 | flat_start_nr | 153.88 | 6 | 536 | 2025-12
2025-12-23 15:00 | flat_start_nr | 149.55 | 5 | 522 | 2025-12
2025-12-23 16:00 | flat_start_nr | 134.83 | 3 | 547 | 2025-12
2025-12-23 17:00 | flat_start_nr | 121.73 | 2 | 540 | 2025-12
2025-12-23 18:00 | flat_start_nr | 123.09 | 2 | 542 | 2025-12
2025-12-23 19:00 | flat_start_nr | 121.05 | 2 | 542 | 2025-12
2025-12-23 20:00 | flat_start_nr | 126.09 | 2 | 541 | 2025-12
2025-12-23 21:00 | flat_start_nr | 112.53 | 1 | 526 | 2025-12
2025-12-23 22:00 | flat_start_nr | 116.37 | 3 | 525 | 2025-12
2025-12-23 23:00 | flat_start_nr | 124.66 | 3 | 526 | 2025-12
2025-12-24 | flat_start_nr | 117 | 3 | 530 | 2025-12
2025-12-24 01:00 | flat_start_nr | 122.43 | 3 | 525 | 2025-12
2025-12-24 02:00 | flat_start_nr | 125.49 | 3 | 526 | 2025-12
2025-12-24 03:00 | flat_start_nr | 134.18 | 4 | 529 | 2025-12
2025-12-24 04:00 | flat_start_nr | 132.35 | 4 | 531 | 2025-12
2025-12-24 05:00 | flat_start_nr | 130.3 | 4 | 531 | 2025-12
2025-12-24 06:00 | flat_start_nr | 127.09 | 3 | 532 | 2025-12
2025-12-24 07:00 | flat_start_nr | 115.45 | 2 | 528 | 2025-12
2025-12-24 08:00 | flat_start_nr | 107.31 | 2 | 528 | 2025-12
2025-12-24 09:00 | flat_start_nr | 117.25 | 3 | 535 | 2025-12
2025-12-24 10:00 | flat_start_nr | 125.23 | 3 | 527 | 2025-12
2025-12-24 11:00 | flat_start_nr | 128.46 | 3 | 529 | 2025-12
2025-12-24 12:00 | flat_start_nr | 122.46 | 3 | 531 | 2025-12
2025-12-24 13:00 | flat_start_nr | 129.8 | 4 | 530 | 2025-12
2025-12-24 14:00 | flat_start_nr | 139.59 | 4 | 524 | 2025-12
2025-12-24 15:00 | flat_start_nr | 133.38 | 4 | 529 | 2025-12
2025-12-24 16:00 | flat_start_nr | 125.72 | 3 | 530 | 2025-12
2025-12-24 17:00 | flat_start_nr | 128.55 | 3 | 535 | 2025-12
2025-12-24 18:00 | flat_start_nr | 134.08 | 4 | 544 | 2025-12
2025-12-24 19:00 | flat_start_nr | 127.29 | 3 | 542 | 2025-12
2025-12-24 20:00 | flat_start_nr | 129.51 | 4 | 535 | 2025-12
2025-12-24 21:00 | flat_start_nr | 122.47 | 3 | 542 | 2025-12
2025-12-24 22:00 | flat_start_nr | 118.16 | 3 | 537 | 2025-12
2025-12-24 23:00 | flat_start_nr | 119.61 | 3 | 536 | 2025-12
2025-12-25 | flat_start_nr | 111.43 | 2 | 531 | 2025-12
2025-12-25 01:00 | flat_start_nr | 110.54 | 2 | 535 | 2025-12
2025-12-25 02:00 | flat_start_nr | 110.12 | 2 | 534 | 2025-12
2025-12-25 03:00 | flat_start_nr | 114.64 | 2 | 532 | 2025-12
2025-12-25 04:00 | flat_start_nr | 118.52 | 3 | 532 | 2025-12
2025-12-25 05:00 | flat_start_nr | 123.36 | 3 | 529 | 2025-12
2025-12-25 06:00 | flat_start_nr | 128.77 | 3 | 536 | 2025-12
2025-12-25 07:00 | flat_start_nr | 142.31 | 5 | 544 | 2025-12
2025-12-25 08:00 | flat_start_nr | 142.78 | 5 | 544 | 2025-12
2025-12-25 09:00 | flat_start_nr | 138.45 | 4 | 540 | 2025-12
2025-12-25 10:00 | flat_start_nr | 133.51 | 4 | 527 | 2025-12
2025-12-25 11:00 | flat_start_nr | 133.86 | 4 | 530 | 2025-12
2025-12-25 12:00 | flat_start_nr | 128.27 | 3 | 524 | 2025-12
2025-12-25 13:00 | flat_start_nr | 134.38 | 4 | 526 | 2025-12
2025-12-25 14:00 | flat_start_nr | 131.01 | 4 | 526 | 2025-12
2025-12-25 15:00 | flat_start_nr | 127.83 | 3 | 524 | 2025-12
2025-12-25 16:00 | flat_start_nr | 111.74 | 2 | 538 | 2025-12
2025-12-25 17:00 | flat_start_nr | 112.47 | 3 | 532 | 2025-12
2025-12-25 18:00 | flat_start_nr | 138.04 | 4 | 544 | 2025-12
2025-12-25 19:00 | flat_start_nr | 133.45 | 4 | 545 | 2025-12
2025-12-25 20:00 | flat_start_nr | 122.5 | 3 | 536 | 2025-12
2025-12-25 21:00 | flat_start_nr | 111.19 | 2 | 533 | 2025-12
2025-12-25 22:00 | flat_start_nr | 117.71 | 3 | 534 | 2025-12
2025-12-25 23:00 | flat_start_nr | 108.61 | 2 | 531 | 2025-12
2025-12-26 | flat_start_nr | 114.61 | 2 | 530 | 2025-12
2025-12-26 01:00 | flat_start_nr | 107.52 | 2 | 533 | 2025-12
2025-12-26 02:00 | flat_start_nr | 112.56 | 2 | 535 | 2025-12
2025-12-26 03:00 | flat_start_nr | 126.2 | 3 | 536 | 2025-12
2025-12-26 04:00 | flat_start_nr | 135.54 | 4 | 544 | 2025-12
2025-12-26 05:00 | flat_start_nr | 135.41 | 4 | 540 | 2025-12
2025-12-26 06:00 | flat_start_nr | 124.5 | 3 | 539 | 2025-12
2025-12-26 07:00 | flat_start_nr | 111.56 | 2 | 534 | 2025-12
2025-12-26 08:00 | flat_start_nr | 112.7 | 2 | 539 | 2025-12
2025-12-26 09:00 | flat_start_nr | 113.66 | 2 | 532 | 2025-12
2025-12-26 10:00 | flat_start_nr | 112.42 | 2 | 535 | 2025-12
2025-12-26 11:00 | flat_start_nr | 111.85 | 2 | 536 | 2025-12
2025-12-26 12:00 | flat_start_nr | 110.79 | 2 | 537 | 2025-12
2025-12-26 13:00 | flat_start_nr | 110.09 | 2 | 538 | 2025-12
2025-12-26 14:00 | flat_start_nr | 114.27 | 2 | 529 | 2025-12
2025-12-26 15:00 | flat_start_nr | 114.23 | 2 | 533 | 2025-12
2025-12-26 16:00 | flat_start_nr | 107.33 | 2 | 533 | 2025-12
2025-12-26 17:00 | flat_start_nr | 107.71 | 1 | 542 | 2025-12
2025-12-26 18:00 | flat_start_nr | 107.95 | 2 | 541 | 2025-12
2025-12-26 19:00 | flat_start_nr | 108.01 | 2 | 534 | 2025-12
2025-12-26 20:00 | flat_start_nr | 107.95 | 2 | 532 | 2025-12
2025-12-26 21:00 | flat_start_nr | 108.01 | 2 | 531 | 2025-12
2025-12-26 22:00 | flat_start_nr | 115.11 | 2 | 529 | 2025-12
2025-12-26 23:00 | flat_start_nr | 134.7 | 4 | 540 | 2025-12
2025-12-27 | flat_start_nr | 141.65 | 4 | 543 | 2025-12
2025-12-27 01:00 | flat_start_nr | 139.57 | 4 | 543 | 2025-12
2025-12-27 02:00 | flat_start_nr | 142.47 | 4 | 548 | 2025-12
2025-12-27 03:00 | flat_start_nr | 143.46 | 5 | 536 | 2025-12
2025-12-27 04:00 | flat_start_nr | 145.61 | 6 | 549 | 2025-12
2025-12-27 05:00 | flat_start_nr | 144.89 | 4 | 544 | 2025-12
2025-12-27 06:00 | flat_start_nr | 157.64 | 5 | 563 | 2025-12
2025-12-27 07:00 | flat_start_nr | 157.19 | 5 | 562 | 2025-12
2025-12-27 16:00 | flat_start_nr | 152.34 | 5 | 533 | 2025-12
2025-12-27 17:00 | flat_start_nr | 130.4 | 5 | 546 | 2025-12
2025-12-27 18:00 | flat_start_nr | 133.34 | 5 | 544 | 2025-12
2025-12-27 19:00 | flat_start_nr | 133.22 | 4 | 543 | 2025-12
2025-12-27 20:00 | flat_start_nr | 133.33 | 4 | 548 | 2025-12
2025-12-27 21:00 | flat_start_nr | 129.69 | 5 | 544 | 2025-12
2025-12-27 22:00 | flat_start_nr | 122.09 | 4 | 541 | 2025-12
2025-12-27 23:00 | flat_start_nr | 112.75 | 2 | 541 | 2025-12
2025-12-28 | flat_start_nr | 118.03 | 3 | 545 | 2025-12
2025-12-28 01:00 | flat_start_nr | 119.85 | 3 | 538 | 2025-12
2025-12-28 02:00 | flat_start_nr | 118.69 | 3 | 531 | 2025-12
2025-12-28 03:00 | flat_start_nr | 114.15 | 2 | 533 | 2025-12
2025-12-28 04:00 | flat_start_nr | 127.01 | 3 | 533 | 2025-12
2025-12-28 05:00 | flat_start_nr | 134.79 | 4 | 538 | 2025-12
2025-12-28 06:00 | flat_start_nr | 141.06 | 4 | 540 | 2025-12
2025-12-28 07:00 | flat_start_nr | 149.99 | 5 | 531 | 2025-12
2025-12-28 17:00 | flat_start_nr | 154.65 | 6 | 528 | 2025-12
2025-12-28 18:00 | flat_start_nr | 154.69 | 6 | 526 | 2025-12
2025-12-28 19:00 | normal_nr | 160.51 | 6 | 555 | 2025-12
2025-12-28 21:00 | flat_start_nr | 152.85 | 7 | 537 | 2025-12
2025-12-28 22:00 | flat_start_nr | 157.79 | 6 | 541 | 2025-12
2025-12-28 23:00 | flat_start_nr | 155.23 | 6 | 533 | 2025-12
2025-12-29 06:00 | flat_start_nr | 158.08 | 7 | 549 | 2025-12
2025-12-29 07:00 | flat_start_nr | 148.48 | 6 | 532 | 2025-12
2025-12-29 17:00 | flat_start_nr | 151.78 | 6 | 526 | 2025-12
2025-12-29 18:00 | flat_start_nr | 155.45 | 7 | 532 | 2025-12
2025-12-29 19:00 | flat_start_nr | 155.92 | 7 | 531 | 2025-12
2025-12-29 20:00 | flat_start_nr | 157.41 | 6 | 563 | 2025-12
2025-12-29 21:00 | flat_start_nr | 151.75 | 6 | 527 | 2025-12
2025-12-30 06:00 | flat_start_nr | 157.34 | 6 | 547 | 2025-12
2025-12-30 07:00 | flat_start_nr | 157.5 | 7 | 548 | 2025-12
2025-12-30 17:00 | flat_start_nr | 137.39 | 6 | 537 | 2025-12
2025-12-30 18:00 | flat_start_nr | 140.11 | 5 | 539 | 2025-12
2025-12-30 19:00 | flat_start_nr | 146.74 | 7 | 535 | 2025-12
2025-12-30 20:00 | flat_start_nr | 148.86 | 7 | 531 | 2025-12
2025-12-30 21:00 | flat_start_nr | 153.28 | 8 | 521 | 2025-12
2025-12-30 22:00 | flat_start_nr | 152.08 | 7 | 521 | 2025-12
2025-12-30 23:00 | flat_start_nr | 152.92 | 6 | 524 | 2025-12
2025-12-31 | flat_start_nr | 146.71 | 5 | 540 | 2025-12
2025-12-31 01:00 | flat_start_nr | 150.81 | 5 | 531 | 2025-12
2025-12-31 02:00 | flat_start_nr | 155.5 | 6 | 546 | 2025-12
2025-12-31 03:00 | flat_start_nr | 149.81 | 5 | 529 | 2025-12
2025-12-31 04:00 | flat_start_nr | 149.71 | 5 | 530 | 2025-12
2025-12-31 05:00 | flat_start_nr | 154.22 | 6 | 549 | 2025-12
2025-12-31 06:00 | flat_start_nr | 156.22 | 6 | 541 | 2025-12
2025-12-31 07:00 | flat_start_nr | 152.88 | 6 | 527 | 2025-12
2025-12-31 17:00 | flat_start_nr | 140.36 | 5 | 538 | 2025-12
2025-12-31 18:00 | flat_start_nr | 145.98 | 6 | 536 | 2025-12
2025-12-31 19:00 | flat_start_nr | 149.71 | 6 | 523 | 2025-12
2025-12-31 20:00 | flat_start_nr | 157.02 | 5 | 537 | 2025-12
2025-12-31 21:00 | flat_start_nr | 157.43 | 5 | 535 | 2025-12
2025-12-31 22:00 | flat_start_nr | 146.28 | 5 | 538 | 2025-12
2025-12-31 23:00 | flat_start_nr | 138.65 | 4 | 544 | 2025-12

## Raw_Thermal_Branch (hidden)
branch | circuits | hours_violated | violation_events | max_pct | avg_pct | min_pct | total_excess_pct_points | first_seen | last_seen | share_of_solved_hours_pct
12-412 | 20 | 4117 | 4117 | 128.89 | 113.9978 | 100.01 | 57628.93 | 2025-01-01 | 2025-12-31 23:00 | 78.9453
159-480 | 14 | 3 | 3 | 122.34 | 107.8633 | 100.6 | 23.59 | 2025-07-26 20:00 | 2025-09-04 15:00 | 0.057526
161-162 | 16 | 1 | 1 | 104.6 | 104.6 | 104.6 | 4.6 | 2025-09-04 15:00 | 2025-09-04 15:00 | 0.019175
171-329 | 77 | 1 | 1 | 102.4 | 102.4 | 102.4 | 2.4 | 2025-09-04 15:00 | 2025-09-04 15:00 | 0.019175
20-39 | 02 | 72 | 72 | 103.07 | 101.2261 | 100.02 | 88.28 | 2025-01-01 07:00 | 2025-01-31 23:00 | 1.3806
20-88 | 40 | 921 | 921 | 107.07 | 102.3774 | 100 | 2189.57 | 2025-01-01 | 2025-12-25 17:00 | 17.6606
31-272 | 10 | 1323 | 1323 | 142.6 | 117.561 | 100 | 23233.14 | 2025-01-04 02:00 | 2025-12-31 19:00 | 25.3691
329-819 | 87 | 789 | 789 | 133.55 | 104.5148 | 100 | 3562.15 | 2025-01-07 11:00 | 2025-12-31 21:00 | 15.1294
4120-558120 | F1 | 40 | 40 | 125.72 | 100.7802 | 100 | 31.21 | 2025-01-22 18:00 | 2025-12-18 22:00 | 0.76702
456-90000 | 01 | 6 | 6 | 119.68 | 105.5483 | 100.63 | 33.29 | 2025-02-13 15:00 | 2025-09-04 15:00 | 0.11505
816-1501 | 87 | 1436 | 1436 | 111.85 | 103.6894 | 100.02 | 5298.01 | 2025-01-07 11:00 | 2025-12-31 22:00 | 27.536
816-817 | 87 | 5128 | 5128 | 165.01 | 136.3184 | 100.01 | 186240.78 | 2025-01-01 | 2025-12-31 23:00 | 98.3317
817-818 | 87 | 4710 | 4710 | 150.72 | 123.0652 | 100.02 | 108637.03 | 2025-01-01 01:00 | 2025-12-31 23:00 | 90.3164
818-819 | 87 | 3617 | 3617 | 139.97 | 114.6918 | 100.01 | 53140.22 | 2025-01-01 03:00 | 2025-12-31 23:00 | 69.3576
873-875 | 79 | 240 | 240 | 102.15 | 101.8269 | 100.11 | 438.45 | 2025-01-11 05:00 | 2025-12-30 22:00 | 4.6021

## Raw_Voltage_Bus (hidden)
bus | bus_name_final | nom_kv | area_num | area_name | planning_area | region | hours_violated | violation_events | high_events | low_events | dominant_type | max_pu | min_pu | avg_pu | first_seen | last_seen
10605 | THICKWD | 23 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.2691 | 1.2414 | 1.2592 | 2025-01-01 | 2025-12-31 23:00
3270 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.2654 | 1.2533 | 1.2598 | 2025-01-01 | 2025-12-31 23:00
1080 | WESLY C4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.131 | 1.1228 | 1.1282 | 2025-01-01 | 2025-12-31 23:00
1655 | DAWES240 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1239 | 1.1209 | 1.1221 | 2025-01-01 | 2025-12-31 23:00
1605 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.12 | 1.12 | 1.12 | 2025-01-01 | 2025-12-31 23:00
1090 | MEIKLE1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1176 | 1.1123 | 1.1154 | 2025-01-01 | 2025-12-31 23:00
204 | MCMILLA4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1174 | 1.1119 | 1.1143 | 2025-01-01 | 2025-12-31 23:00
1050 | HOTCHKS7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1173 | 1.112 | 1.1152 | 2025-01-01 | 2025-12-31 23:00
1083 | CARMON 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1168 | 1.108 | 1.114 | 2025-01-01 | 2025-12-31 23:00
1280 | BRINT02 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1165 | 1.1021 | 1.11 | 2025-01-01 | 2025-12-31 23:00
747 | WT_144 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1158 | 1.1094 | 1.1139 | 2025-01-01 | 2025-12-31 23:00
850 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1158 | 1.1094 | 1.1139 | 2025-01-01 | 2025-12-31 23:00
1041 | BUCHN C7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1157 | 1.11 | 1.1136 | 2025-01-01 | 2025-12-31 23:00
920 | ROUND01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1155 | 1.1089 | 1.112 | 2025-01-01 | 2025-12-31 23:00
1082 | WESLY C7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1148 | 1.1083 | 1.1128 | 2025-01-01 | 2025-12-31 23:00
1052 | HAMBURG7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1144 | 1.112 | 1.1135 | 2025-01-01 | 2025-12-31 23:00
1602 | LIVOCKPS | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1141 | 1.0993 | 1.1071 | 2025-01-01 | 2025-12-31 23:00
381 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.114 | 1.0972 | 1.1042 | 2025-01-01 | 2025-12-31 23:00
348 | LEISMER4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1138 | 1.1079 | 1.1107 | 2025-01-01 | 2025-12-31 23:00
867 | INGLIS 1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1133 | 1.1129 | 1.1131 | 2025-01-01 | 2025-12-31 23:00
868 | INGLIS 2 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1133 | 1.1129 | 1.1131 | 2025-01-01 | 2025-12-31 23:00
1226 | WABASCA4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1128 | 1.1002 | 1.1072 | 2025-01-01 | 2025-12-31 23:00
14055 | LLOYD 9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1121 | 1.0944 | 1.1061 | 2025-01-01 | 2025-12-31 23:00
767 | VOY260 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.112 | 1.1116 | 1.1118 | 2025-01-01 | 2025-12-31 23:00
1291 | KETL RV4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1119 | 1.1068 | 1.1091 | 2025-01-01 | 2025-12-31 23:00
405 | CONKLIN1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1111 | 1.1059 | 1.1085 | 2025-01-01 | 2025-12-31 23:00
1949 | ILAKE_01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1108 | 1.1042 | 1.1074 | 2025-01-01 | 2025-12-31 23:00
282 | HEARTLAK | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1095 | 1.1023 | 1.1057 | 2025-01-01 | 2025-12-31 23:00
1044 | KEMP RV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1095 | 1.1061 | 1.1083 | 2025-01-01 | 2025-12-31 23:00
1211 | MILLENN8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1089 | 1.1084 | 1.1086 | 2025-01-01 | 2025-12-31 23:00
1215 | HORSE 18 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1089 | 1.1084 | 1.1086 | 2025-01-01 | 2025-12-31 23:00
1216 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1089 | 1.1084 | 1.1086 | 2025-01-01 | 2025-12-31 23:00
1689 | TARSLDC | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1085 | 1.108 | 1.1082 | 2025-01-01 | 2025-12-31 23:00
974 | PIKE_01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.108 | 1.1018 | 1.1048 | 2025-01-01 | 2025-12-31 23:00
16241 | LONGLK16 4.2000 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.108 | 1.1068 | 1.1073 | 2025-01-01 | 2025-12-31 23:00
1055 | CADOTTE7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1076 | 1.104 | 1.1064 | 2025-01-01 | 2025-12-31 23:00
1225 | TARSLDA | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1076 | 1.1071 | 1.1074 | 2025-01-01 | 2025-12-31 23:00
369 | CHRISLK1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1072 | 1.1013 | 1.1041 | 2025-01-01 | 2025-12-31 23:00
1223 | TARSLDB | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1072 | 1.1067 | 1.107 | 2025-01-01 | 2025-12-31 23:00
1288 | LIVOCK01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1072 | 1.0906 | 1.099 | 2025-01-01 | 2025-12-31 23:00
1245 | KINOSIS1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1071 | 1.1035 | 1.1049 | 2025-01-01 | 2025-12-31 23:00
1053 | RING CK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1066 | 1.105 | 1.106 | 2025-01-01 | 2025-12-31 23:00
603 | GHOSTPI1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1065 | 1.0855 | 1.1019 | 2025-01-01 | 2025-12-31 23:00
138 | N BARRH4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1064 | 1.0987 | 1.1028 | 2025-01-01 | 2025-12-31 23:00
16220 | MIL_GT3 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1062 | 1.1057 | 1.1059 | 2025-01-01 | 2025-12-31 23:00
1228 | MITS E.4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.106 | 1.0988 | 1.1034 | 2025-01-01 | 2025-12-31 23:00
878 | JFISH01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1059 | 1.1 | 1.1029 | 2025-01-01 | 2025-12-31 23:00
1218 | STEEPBNK | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1058 | 1.1054 | 1.1056 | 2025-01-01 | 2025-12-31 23:00
1423 | NEVIS 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1056 | 1.0854 | 1.0997 | 2025-01-01 | 2025-12-31 23:00
1208 | MILLENN4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1051 | 1.1045 | 1.1048 | 2025-01-01 | 2025-12-31 23:00
1212 | MIL_G5 4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1051 | 1.1045 | 1.1048 | 2025-01-01 | 2025-12-31 23:00
1213 | MIL_G6 4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1051 | 1.1045 | 1.1048 | 2025-01-01 | 2025-12-31 23:00
1085 | PEACE RV | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.105 | 1.0979 | 1.1031 | 2025-01-01 | 2025-12-31 23:00
1313 | MARG LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1047 | 1.1007 | 1.1025 | 2025-01-01 | 2025-12-31 23:00
602 | GHOSTPI3 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1046 | 1.0843 | 1.1002 | 2025-01-01 | 2025-12-31 23:00
902 | BCKSP_01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1046 | 1.0987 | 1.1016 | 2025-01-01 | 2025-12-31 23:00
1429 | 948S_HV | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1044 | 1.0858 | 1.1 | 2025-01-01 | 2025-12-31 23:00
1200 | RUTH LK4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1042 | 1.1034 | 1.1038 | 2025-01-01 | 2025-12-31 23:00
1214 | EDD34 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1042 | 1.1036 | 1.1039 | 2025-01-01 | 2025-12-31 23:00
18491 | STNB AUX | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1042 | 1.0953 | 1.1005 | 2025-01-01 | 2025-12-31 23:00
1036 | KEG RVR7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1041 | 1.1014 | 1.1031 | 2025-01-01 | 2025-12-31 23:00
1334 | 29EDD-55 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1038 | 1.1033 | 1.1036 | 2025-01-01 | 2025-12-31 23:00
1205 | SYNC_D04 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1033 | 1.1025 | 1.1029 | 2025-01-01 | 2025-12-31 23:00
879 | 539S_240 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1031 | 1.0972 | 1.1001 | 2025-01-01 | 2025-12-31 23:00
1688 | EDD56-1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1029 | 1.1023 | 1.1025 | 2025-01-01 | 2025-12-31 23:00
1301 | FOSTERCK | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1027 | 1.1012 | 1.102 | 2025-01-01 | 2025-12-31 23:00
1677 | EDD56 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1027 | 1.1021 | 1.1023 | 2025-01-01 | 2025-12-31 23:00
1206 | AURORA 4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1026 | 1.102 | 1.1023 | 2025-01-01 | 2025-12-31 23:00
1676 | EDD651 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1024 | 1.102 | 1.1022 | 2025-01-01 | 2025-12-31 23:00
18055 | CADOTTA9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1023 | 1.0987 | 1.1011 | 2025-01-01 | 2025-12-31 23:00
19055 | CADOTTE9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1023 | 1.0987 | 1.1011 | 2025-01-01 | 2025-12-31 23:00
1462 | YEO240 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1009 | 1.0915 | 1.0963 | 2025-01-01 | 2025-12-31 23:00
1670 | BWC01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1009 | 1.0915 | 1.0963 | 2025-01-01 | 2025-12-31 23:00
1034 | CHINCHA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1007 | 1.0988 | 1.1 | 2025-01-01 | 2025-12-31 23:00
1626 | AMR_01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1007 | 1.0913 | 1.0961 | 2025-01-01 | 2025-12-31 23:00
1669 | AMR_02 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1007 | 1.0913 | 1.0961 | 2025-01-01 | 2025-12-31 23:00
1508 | KLC_TAP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1004 | 1.1002 | 1.1003 | 2025-01-01 | 2025-12-31 23:00
1510 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1004 | 1.1002 | 1.1003 | 2025-01-01 | 2025-12-31 23:00
1351 | NABIYE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1002 | 1.098 | 1.0993 | 2025-01-01 | 2025-12-31 23:00
1300 | WOLF LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.1 | 1.0965 | 1.0984 | 2025-01-01 | 2025-12-31 23:00
560026 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1 | 1.1 | 1.1 | 2025-01-01 | 2025-12-31 23:00
561026 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1 | 1.1 | 1.1 | 2025-01-01 | 2025-12-31 23:00
562026 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.1 | 1.1 | 1.1 | 2025-01-01 | 2025-12-31 23:00
13241 | LONGLK13 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0998 | 1.0984 | 1.099 | 2025-01-01 | 2025-12-31 23:00
1016 | FORT NE7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0997 | 1.0996 | 1.0997 | 2025-01-01 | 2025-12-31 23:00
14241 | LONGLK14 13.800 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0997 | 1.0985 | 1.099 | 2025-01-01 | 2025-12-31 23:00
1307 | PRIMEAST | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0992 | 1.0917 | 1.0977 | 2025-01-01 | 2025-12-31 23:00
17307 |  | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0992 | 1.0917 | 1.0977 | 2025-01-01 | 2025-12-31 23:00
1017 | WSP_138 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.099 | 1.099 | 1.099 | 2025-01-01 | 2025-12-31 23:00
1302 | PRIMROSE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0988 | 1.0914 | 1.0974 | 2025-01-01 | 2025-12-31 23:00
18241 | LONGLK18 13.800 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0987 | 1.0973 | 1.0979 | 2025-01-01 | 2025-12-31 23:00
1402 | SALTCR1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0983 | 1.0951 | 1.0967 | 2025-01-01 | 2025-12-31 23:00
800 | PRIM TAP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.098 | 1.0943 | 1.0965 | 2025-01-01 | 2025-12-31 23:00
213 | HAIGRIVE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0976 | 1.0962 | 1.0971 | 2025-01-01 | 2025-12-31 23:00
666 | DOVER | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0971 | 1.0947 | 1.0959 | 2025-01-01 | 2025-12-31 23:00
1060 | NORCEN 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.097 | 1.0945 | 1.0963 | 2025-01-01 | 2025-12-31 23:00
1075 | SEAL LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0969 | 1.0936 | 1.0959 | 2025-01-01 | 2025-12-31 23:00
4405 | CONKLIN3 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0964 | 1.091 | 1.0937 | 2025-01-01 | 2025-12-31 23:00
1433 | 3 HILLS7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0962 | 1.0773 | 1.092 | 2025-01-01 | 2025-12-31 23:00
1274 | MACKAY | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0959 | 1.0933 | 1.0946 | 2025-01-01 | 2025-12-31 23:00
1632 | BADLAND1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0958 | 1.0881 | 1.0925 | 2025-01-01 | 2025-12-31 23:00
4015 | MTN COA9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0958 | 1.0825 | 1.0917 | 2025-01-01 | 2025-12-31 23:00
1646 | PARKER1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0957 | 1.088 | 1.0924 | 2025-01-01 | 2025-12-31 23:00
488 | CHERHIL1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0956 | 1.0876 | 1.0914 | 2025-01-01 | 2025-12-31 23:00
1315 | LACOREY7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0954 | 1.0902 | 1.093 | 2025-01-01 | 2025-12-31 23:00
1436 | 768S_HV | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0948 | 1.0807 | 1.0914 | 2025-01-01 | 2025-12-31 23:00
1018 | BASSET 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0945 | 1.0934 | 1.0941 | 2025-01-01 | 2025-12-31 23:00
1304 | MAHNO1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0944 | 1.0913 | 1.0931 | 2025-01-01 | 2025-12-31 23:00
1460 | WINT HI7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0943 | 1.086 | 1.0915 | 2025-01-01 | 2025-12-31 23:00
10676 | EDD65M1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0941 | 1.0938 | 1.0939 | 2025-01-01 | 2025-12-31 23:00
11676 | EDD65M2 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0941 | 1.0938 | 1.094 | 2025-01-01 | 2025-12-31 23:00
248 | MAHKESES | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0939 | 1.0913 | 1.0928 | 2025-01-01 | 2025-12-31 23:00
1428 | 769_HVR | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0939 | 1.0729 | 1.0871 | 2025-01-01 | 2025-12-31 23:00
1448 | MICH. C7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0937 | 1.0851 | 1.0911 | 2025-01-01 | 2025-12-31 23:00
759 | WINTHV | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0936 | 1.0849 | 1.0908 | 2025-01-01 | 2025-12-31 23:00
19344 | BONNY 9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0929 | 1.0851 | 1.0902 | 2025-01-01 | 2025-12-31 23:00
1180 | GOOSE R7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0923 | 1.0885 | 1.0912 | 2025-01-01 | 2025-12-31 23:00
1229 | MITS E.7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.092 | 1.0858 | 1.0896 | 2025-01-01 | 2025-12-31 23:00
1234 | OTAUWAU7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0917 | 1.0854 | 1.0893 | 2025-01-01 | 2025-12-31 23:00
1230 | AEC MILL | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0916 | 1.0854 | 1.0892 | 2025-01-01 | 2025-12-31 23:00
1485 | ANDERSON | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0916 | 1.0825 | 1.0882 | 2025-01-01 | 2025-12-31 23:00
1105 | FRIEDEN7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0915 | 1.0872 | 1.0905 | 2025-01-01 | 2025-12-31 23:00
1348 | WHITFISH | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0915 | 1.0829 | 1.0868 | 2025-01-01 | 2025-12-31 23:00
1275 | VIRGINI7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0911 | 1.0848 | 1.0891 | 2025-01-01 | 2025-12-31 23:00
1463 | BULLPON7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.091 | 1.0854 | 1.089 | 2025-01-01 | 2025-12-31 23:00
19419 | PEMUKN3 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0908 | 1.0872 | 1.0893 | 2025-01-01 | 2025-12-31 23:00
1344 | BONNY 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0907 | 1.083 | 1.0881 | 2025-01-01 | 2025-12-31 23:00
1026 | ZAMA LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0906 | 1.09 | 1.0904 | 2025-01-01 | 2025-12-31 23:00
1261 | LOU CR.7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0904 | 1.0835 | 1.088 | 2025-01-01 | 2025-12-31 23:00
1077 | 7L23 TAP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0901 | 1.0848 | 1.0883 | 2025-01-01 | 2025-12-31 23:00
1284 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0901 | 1.0848 | 1.0883 | 2025-01-01 | 2025-12-31 23:00
552340 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0901 | 1.0757 | 1.0872 | 2025-01-01 | 2025-12-31 23:00
563002 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0901 | 1.0804 | 1.0867 | 2025-01-01 | 2025-12-31 23:00
565002 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0901 | 1.0804 | 1.0867 | 2025-01-01 | 2025-12-31 23:00
14 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.09 | 1.09 | 2025-01-01 | 2025-12-31 23:00
1150 | DONNELL7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.0847 | 1.0886 | 2025-01-01 | 2025-12-31 23:00
1164 | L.SMOKY7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.09 | 1.09 | 2025-01-01 | 2025-12-31 23:00
1165 | STURGEO7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.09 | 1.09 | 2025-01-01 | 2025-12-31 23:00
1172 | STURG_1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.09 | 1.09 | 2025-01-01 | 2025-12-31 23:00
1303 | MAHIHKA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.0866 | 1.0885 | 2025-01-01 | 2025-12-31 23:00
1309 | BOURQUE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.09 | 1.0866 | 1.0885 | 2025-01-01 | 2025-12-31 23:00
1421 | COYTLK1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0899 | 1.0816 | 1.0868 | 2025-01-01 | 2025-12-31 23:00
2030 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0898 | 1.0782 | 1.0835 | 2025-01-01 | 2025-12-31 23:00
1088 | DAISHOW7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0894 | 1.0829 | 1.0877 | 2025-01-01 | 2025-12-31 23:00
1509 | FNC_TAP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0894 | 1.0891 | 1.0893 | 2025-01-01 | 2025-12-31 23:00
561002 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0894 | 1.0797 | 1.0859 | 2025-01-01 | 2025-12-31 23:00
1065 | LUBICON7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0893 | 1.0873 | 1.0887 | 2025-01-01 | 2025-12-31 23:00
19241 | LONGLK19 4.2000 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0892 | 1.0878 | 1.0884 | 2025-01-01 | 2025-12-31 23:00
1471 | MONITOR7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0891 | 1.0854 | 1.0875 | 2025-01-01 | 2025-12-31 23:00
1511 | FNC-1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0889 | 1.0886 | 1.0888 | 2025-01-01 | 2025-12-31 23:00
20000 | BC BORDE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0884 | 1.0881 | 1.0883 | 2025-01-01 | 2025-12-31 23:00
1270 | ESSO JU7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0883 | 1.0814 | 1.0859 | 2025-01-01 | 2025-12-31 23:00
1271 | MORSE RV | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0883 | 1.0814 | 1.0859 | 2025-01-01 | 2025-12-31 23:00
557690 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0883 | 1.0782 | 1.0835 | 2025-01-01 | 2025-12-31 23:00
1243 | EDITH L7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0882 | 1.0813 | 1.0858 | 2025-01-01 | 2025-12-31 23:00
1155 | VALLEYV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0881 | 1.0878 | 1.088 | 2025-01-01 | 2025-12-31 23:00
1310 | LEMING 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0881 | 1.0849 | 1.0867 | 2025-01-01 | 2025-12-31 23:00
1458 | LOYALIS7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.088 | 1.0843 | 1.0864 | 2025-01-01 | 2025-12-31 23:00
17218 | SUNC_R67 | 13.8 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.088 | 1.0876 | 1.0878 | 2025-01-01 | 2025-12-31 23:00
1260 | LOU CR.4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0877 | 1.08 | 1.0851 | 2025-01-01 | 2025-12-31 23:00
1023 | SULPH PT | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0876 | 1.0869 | 1.0873 | 2025-01-01 | 2025-12-31 23:00
1447 | 963S_HV | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0874 | 1.0786 | 1.0846 | 2025-01-01 | 2025-12-31 23:00
1439 | STETTLE8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0873 | 1.0761 | 1.0844 | 2025-01-01 | 2025-12-31 23:00
18477 | RIBSTON7 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0873 | 1.0835 | 1.0857 | 2025-01-01 | 2025-12-31 23:00
12241 | LONGLK10 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0868 | 1.0857 | 1.0861 | 2025-01-01 | 2025-12-31 23:00
1272 | FIELDGA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0867 | 1.0798 | 1.0843 | 2025-01-01 | 2025-12-31 23:00
1318 | 7LA24_TP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0864 | 1.0795 | 1.084 | 2025-01-01 | 2025-12-31 23:00
1285 | NIPISI 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0863 | 1.0822 | 1.085 | 2025-01-01 | 2025-12-31 23:00
542002 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0861 | 1.0764 | 1.0827 | 2025-01-01 | 2025-12-31 23:00
547102 | 9LA59TAP | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0861 | 1.0764 | 1.0826 | 2025-01-01 | 2025-12-31 23:00
777 | ED1000-1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0859 | 1.0821 | 1.0845 | 2025-01-01 | 2025-12-31 23:00
778 | ED1000-2 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0859 | 1.082 | 1.0844 | 2025-01-01 | 2025-12-31 23:00
249 | 878S | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0856 | 1.0856 | 1.0856 | 2025-01-01 | 2025-12-31 23:00
1112 | BEARTRA1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0856 | 1.0787 | 1.0832 | 2025-01-01 | 2025-12-31 23:00
1277 | BLK_FLY1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0855 | 1.0799 | 1.0835 | 2025-01-01 | 2025-12-31 23:00
1612 | SECORD01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0852 | 1.0814 | 1.0838 | 2025-01-01 | 2025-12-31 23:00
1266 | SARAH L7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0851 | 1.0782 | 1.0827 | 2025-01-01 | 2025-12-31 23:00
1481 | SHEER 14 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.085 | 1.0755 | 1.0819 | 2025-01-01 | 2025-12-31 23:00
1276 | S-SHINE1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0849 | 1.0793 | 1.0829 | 2025-01-01 | 2025-12-31 23:00
1286 | S-SHINE4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0849 | 1.0793 | 1.0829 | 2025-01-01 | 2025-12-31 23:00
1405 | SALTCR2 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0849 | 1.082 | 1.0834 | 2025-01-01 | 2025-12-31 23:00
1440 | OAKLND1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0847 | 1.0755 | 1.0817 | 2025-01-01 | 2025-12-31 23:00
1484 | ANDERSO4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.0749 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
1486 | SHEER 24 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.075 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
75001 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.0749 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
75002 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.0749 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
75501 | SOL21C_01_2 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.0749 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
75502 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0845 | 1.0749 | 1.0814 | 2025-01-01 | 2025-12-31 23:00
1393 | HILL 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0842 | 1.0669 | 1.0784 | 2025-01-01 | 2025-12-31 23:00
1038 | OSB-TAP7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0841 | 1.0839 | 1.084 | 2025-01-01 | 2025-12-31 23:00
1207 | AURORA 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0841 | 1.0837 | 1.0839 | 2025-01-01 | 2025-12-31 23:00
1039 | MELITO7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.084 | 1.0838 | 1.084 | 2025-01-01 | 2025-12-31 23:00
1680 | BITUMONT | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0839 | 1.0805 | 1.0825 | 2025-01-01 | 2025-12-31 23:00
19218 | SUNC_R68 | 13.8 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0839 | 1.0834 | 1.0836 | 2025-01-01 | 2025-12-31 23:00
90 | BICKERD4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0838 | 1.0781 | 1.0805 | 2025-01-01 | 2025-12-31 23:00
549014 | WHISKY1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0838 | 1.0782 | 1.0805 | 2025-01-01 | 2025-12-31 23:00
1163 | L. SMOKY | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0835 | 1.0775 | 1.082 | 2025-01-01 | 2025-12-31 23:00
1020 | HIGH LV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.083 | 1.083 | 1.083 | 2025-01-01 | 2025-12-31 23:00
1406 | SULLV LK | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0829 | 1.0662 | 1.0747 | 2025-01-01 | 2025-12-31 23:00
18511 | FNC-2 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0829 | 1.0825 | 1.0827 | 2025-01-01 | 2025-12-31 23:00
1455 | LLOYD 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0826 | 1.0658 | 1.0769 | 2025-01-01 | 2025-12-31 23:00
18291 | KETL RV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0826 | 1.0776 | 1.0799 | 2025-01-01 | 2025-12-31 23:00
1470 | VETERAN7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0825 | 1.0789 | 1.081 | 2025-01-01 | 2025-12-31 23:00
795 | LINDB_TP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0816 | 1.0643 | 1.0765 | 2025-01-01 | 2025-12-31 23:00
1687 | BOHN_01 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0814 | 1.0765 | 1.0787 | 2025-01-01 | 2025-12-31 23:00
19511 | FNC-3 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0811 | 1.0808 | 1.081 | 2025-01-01 | 2025-12-31 23:00
1418 | LANESLK2 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0807 | 1.0727 | 1.0772 | 2025-01-01 | 2025-12-31 23:00
135 | SUNDANC4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
1263 | JOSLYN4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.078 | 1.0793 | 2025-01-01 | 2025-12-31 23:00
1442 | BIG VAL8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0692 | 1.0776 | 2025-01-01 | 2025-12-31 23:00
2135 | SUNDANB9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
2144 | SUNDAND9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
3144 | SUNDANK9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
4135 | SUNDANJ9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
4144 | SUNDANG9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0805 | 1.0722 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
1444 | LINDBER7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0803 | 1.0629 | 1.0751 | 2025-01-01 | 2025-12-31 23:00
1412 | LANESLK1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0801 | 1.0721 | 1.0766 | 2025-01-01 | 2025-12-31 23:00
1435 | HALKIRK1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0801 | 1.0721 | 1.0766 | 2025-01-01 | 2025-12-31 23:00
4114 | LACOMBE9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0801 | 1.0687 | 1.0779 | 2025-01-01 | 2025-12-31 23:00
1054 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.08 | 1.08 | 1.08 | 2025-01-01 | 2025-12-31 23:00
1070 | CRANBER7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.08 | 1.08 | 1.08 | 2025-01-01 | 2025-12-31 23:00
1320 | ETHEL L7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.08 | 1.0759 | 1.0783 | 2025-01-01 | 2025-12-31 23:00
11669 | AMR8002A | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.08 | 1.0707 | 1.0754 | 2025-01-01 | 2025-12-31 23:00
1614 | HTHFIELD | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0798 | 1.061 | 1.0684 | 2025-01-01 | 2025-12-31 23:00
1615 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0798 | 1.061 | 1.0684 | 2025-01-01 | 2025-12-31 23:00
273 | HRTLAND | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0797 | 1.0609 | 1.0683 | 2025-01-01 | 2025-12-31 23:00
262 | DOME EM4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0796 | 1.0665 | 1.075 | 2025-01-01 | 2025-12-31 23:00
1102 | BOUCH C7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0796 | 1.076 | 1.0787 | 2025-01-01 | 2025-12-31 23:00
1312 | MARG LK4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0796 | 1.0725 | 1.0758 | 2025-01-01 | 2025-12-31 23:00
309 | MCMILLA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0795 | 1.0737 | 1.0761 | 2025-01-01 | 2025-12-31 23:00
1202 | RUTH LA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0795 | 1.0778 | 1.0786 | 2025-01-01 | 2025-12-31 23:00
17241 | LONGLK17 13.800 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0795 | 1.0781 | 1.0786 | 2025-01-01 | 2025-12-31 23:00
677 | CYPRES2 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0794 | 1.0663 | 1.0748 | 2025-01-01 | 2025-12-31 23:00
1224 | HANGSTO7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0794 | 1.0766 | 1.0779 | 2025-01-01 | 2025-12-31 23:00
1431 | TNCHBRY1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0793 | 1.0713 | 1.0759 | 2025-01-01 | 2025-12-31 23:00
76003 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0793 | 1.0713 | 1.0759 | 2025-01-01 | 2025-12-31 23:00
76503 | B24C_01_2 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0793 | 1.0713 | 1.0759 | 2025-01-01 | 2025-12-31 23:00
163 | SAGITAW4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0792 | 1.0707 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
1627 | 7LA97_TP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0792 | 1.0765 | 1.0778 | 2025-01-01 | 2025-12-31 23:00
1673 | HALF_01 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0792 | 1.0765 | 1.0778 | 2025-01-01 | 2025-12-31 23:00
1336 | HIGHPR9 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0791 | 1.0761 | 1.0783 | 2025-01-01 | 2025-12-31 23:00
15241 | LONGLK15 13.800 |  | 25 | FORT MCM |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0791 | 1.0777 | 1.0783 | 2025-01-01 | 2025-12-31 23:00
1028 | RBW LAK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.079 | 1.0786 | 1.0789 | 2025-01-01 | 2025-12-31 23:00
1227 | CROWLK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.079 | 1.0733 | 1.0756 | 2025-01-01 | 2025-12-31 23:00
19102 | BOUCH C9 | 14.4 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.079 | 1.0753 | 1.0781 | 2025-01-01 | 2025-12-31 23:00
83 | RBCUPIL7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0789 | 1.0784 | 1.0787 | 2025-01-01 | 2025-12-31 23:00
1610 | MCCLE_01 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0789 | 1.0723 | 1.0768 | 2025-01-01 | 2025-12-31 23:00
1603 | KEARL240 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0788 | 1.0722 | 1.0767 | 2025-01-01 | 2025-12-31 23:00
1387 | KITSCOT7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0787 | 1.06 | 1.0729 | 2025-01-01 | 2025-12-31 23:00
1151 | 7L48TAP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0781 | 1.0755 | 1.0775 | 2025-01-01 | 2025-12-31 23:00
1332 | GRND CTR | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0781 | 1.0727 | 1.0761 | 2025-01-01 | 2025-12-31 23:00
1153 | TRIANGL7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0779 | 1.0753 | 1.0772 | 2025-01-01 | 2025-12-31 23:00
1477 | RIBSTON1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0775 | 1.0738 | 1.0759 | 2025-01-01 | 2025-12-31 23:00
1089 | DAISHOW9 13.800 |  | 19 | PEACE RI | 19 | Northwest | 5215 | 5215 | 5215 | 0 | High | 1.0774 | 1.0725 | 1.0761 | 2025-01-01 | 2025-12-31 23:00
4331 | VIOL GR9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0774 | 1.059 | 1.0645 | 2025-01-01 | 2025-12-31 23:00
19468 | VETERAN9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0773 | 1.0737 | 1.0758 | 2025-01-01 | 2025-12-31 23:00
2031 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0771 | 1.067 | 1.0716 | 2025-01-01 | 2025-12-31 23:00
1166 | STURGEO8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0768 | 1.0768 | 1.0768 | 2025-01-01 | 2025-12-31 23:00
1251 | HORMIN1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0767 | 1.0743 | 1.0755 | 2025-01-01 | 2025-12-31 23:00
1427 | NILREM3 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0765 | 1.0726 | 1.0747 | 2025-01-01 | 2025-12-31 23:00
1262 | HORUP1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0764 | 1.074 | 1.0752 | 2025-01-01 | 2025-12-31 23:00
1499 | CORDEL 4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0764 | 1.0689 | 1.0731 | 2025-01-01 | 2025-12-31 23:00
1403 | PAINTRT4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0763 | 1.0707 | 1.0737 | 2025-01-01 | 2025-12-31 23:00
1469 | BAT RV79 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0763 | 1.0689 | 1.073 | 2025-01-01 | 2025-12-31 23:00
1489 | BAT RV80 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0763 | 1.0689 | 1.0731 | 2025-01-01 | 2025-12-31 23:00
623 | SUNNYB2 | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0758 | 1.0618 | 1.0667 | 2025-01-01 | 2025-12-31 23:00
630 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0758 | 1.0618 | 1.0667 | 2025-01-01 | 2025-12-31 23:00
392 | ALPAC1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0757 | 1.0709 | 1.0736 | 2025-01-01 | 2025-12-31 23:00
525 | GENESEE4 | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0757 | 1.0618 | 1.0667 | 2025-01-01 | 2025-12-31 23:00
75004 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0757 | 1.0618 | 1.0667 | 2025-01-01 | 2025-12-31 23:00
75504 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0757 | 1.0618 | 1.0667 | 2025-01-01 | 2025-12-31 23:00
17458 | LOYALIS8 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0756 | 1.0718 | 1.074 | 2025-01-01 | 2025-12-31 23:00
19429 | 948S_LV | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0756 | 1.0574 | 1.0714 | 2025-01-01 | 2025-12-31 23:00
258 | ELLERSLI | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0749 | 1.0572 | 1.064 | 2025-01-01 | 2025-12-31 23:00
17075 | SEAL LK8 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0748 | 1.0715 | 1.0738 | 2025-01-01 | 2025-12-31 23:00
510 | KEEPHIL3 | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0746 | 1.06 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
610 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0746 | 1.06 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
76001 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0746 | 1.06 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
76501 | B22E_01_2 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0746 | 1.06 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
270 | SUFFIEL7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0745 | 1.0595 | 1.0676 | 2025-01-01 | 2025-12-31 23:00
260 | JENNER 4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0741 | 1.0613 | 1.0701 | 2025-01-01 | 2025-12-31 23:00
1377 | IRISH C7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.074 | 1.0535 | 1.0681 | 2025-01-01 | 2025-12-31 23:00
60831 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0738 | 1.0728 | 1.0732 | 2025-01-01 | 2025-12-31 23:00
62831 | SEDALIA4 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0738 | 1.0728 | 1.0732 | 2025-01-01 | 2025-12-31 23:00
557113 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0736 | 1.0617 | 1.0713 | 2025-01-01 | 2025-12-31 23:00
19180 | GOOSE R9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0734 | 1.0696 | 1.0723 | 2025-01-01 | 2025-12-31 23:00
4085 | MILLAR 9 13.800 |  | 26 | SWAN HIL |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0732 | 1.062 | 1.0673 | 2025-01-01 | 2025-12-31 23:00
716 | LAKESEN7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.073 | 1.0693 | 1.0714 | 2025-01-01 | 2025-12-31 23:00
1203 | RUTH LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.073 | 1.0713 | 1.0721 | 2025-01-01 | 2025-12-31 23:00
67831 | SEDALIA2 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0728 | 1.0718 | 1.0723 | 2025-01-01 | 2025-12-31 23:00
225 | WARE JCT | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0725 | 1.0567 | 1.0677 | 2025-01-01 | 2025-12-31 23:00
1242 | KINOSIS2 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0725 | 1.0702 | 1.0711 | 2025-01-01 | 2025-12-31 23:00
11236 | MUSKEG5 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0725 | 1.0715 | 1.072 | 2025-01-01 | 2025-12-31 23:00
1437 | MARION 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0722 | 1.0626 | 1.069 | 2025-01-01 | 2025-12-31 23:00
1491 | BAT. RV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0722 | 1.0636 | 1.0686 | 2025-01-01 | 2025-12-31 23:00
67308 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0722 | 1.0522 | 1.0662 | 2025-01-01 | 2025-12-31 23:00
68308 | GRIZZ_L2 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0722 | 1.0522 | 1.0662 | 2025-01-01 | 2025-12-31 23:00
69308 | GRIZZ_L1 | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0721 | 1.0521 | 1.0662 | 2025-01-01 | 2025-12-31 23:00
563026 | TRAVERS_2A | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0721 | 1.0651 | 1.0707 | 2025-01-01 | 2025-12-31 23:00
564026 | TRAVERS_2B | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0721 | 1.0651 | 1.0707 | 2025-01-01 | 2025-12-31 23:00
551489 | BAT RV 9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.072 | 1.063 | 1.0685 | 2025-01-01 | 2025-12-31 23:00
565026 | TRAVERS_2C | 34.5 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.072 | 1.065 | 1.0706 | 2025-01-01 | 2025-12-31 23:00
1372 | ST. PAU7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0715 | 1.0609 | 1.0681 | 2025-01-01 | 2025-12-31 23:00
179 | MARIANA7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0714 | 1.0671 | 1.0688 | 2025-01-01 | 2025-12-31 23:00
18444 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0713 | 1.0599 | 1.0668 | 2025-01-01 | 2025-12-31 23:00
87 | METIS644 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0712 | 1.0701 | 1.0701 | 2025-01-01 | 2025-12-31 23:00
1147 | HR MILN7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0712 | 1.0671 | 1.0705 | 2025-01-01 | 2025-12-31 23:00
298 | ALB NEWS | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0711 | 1.0639 | 1.068 | 2025-01-01 | 2025-12-31 23:00
649 | HANSMAN7 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0711 | 1.07 | 1.07 | 2025-01-01 | 2025-12-31 23:00
831 | SEDALIA1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0711 | 1.0701 | 1.0706 | 2025-01-01 | 2025-12-31 23:00
1413 | N_BRIGDEN | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0711 | 1.0701 | 1.0706 | 2025-01-01 | 2025-12-31 23:00
1466 | CORO JCT | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0711 | 1.0541 | 1.0628 | 2025-01-01 | 2025-12-31 23:00
1438 | LANFIN1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.071 | 1.071 | 1.071 | 2025-01-01 | 2025-12-31 23:00
1149 | KAKWA1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0707 | 1.0669 | 1.0701 | 2025-01-01 | 2025-12-31 23:00
1236 | MUSKEG1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0707 | 1.0684 | 1.0696 | 2025-01-01 | 2025-12-31 23:00
1125 | STEELE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0706 | 1.0506 | 1.0647 | 2025-01-01 | 2025-12-31 23:00
1308 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0706 | 1.0506 | 1.0647 | 2025-01-01 | 2025-12-31 23:00
1476 | YOUNGST8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0704 | 1.0615 | 1.0666 | 2025-01-01 | 2025-12-31 23:00
1622 | TWR_RD1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0704 | 1.0681 | 1.0692 | 2025-01-01 | 2025-12-31 23:00
25336 | VIC R4 | 14.4 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0704 | 1.0571 | 1.0651 | 2025-01-01 | 2025-12-31 23:00
798 | HALSBURY | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0702 | 1.0592 | 1.0668 | 2025-01-01 | 2025-12-31 23:00
1246 | LNGLKC02 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0702 | 1.0689 | 1.0694 | 2025-01-01 | 2025-12-31 23:00
1249 | LNGLKC01 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0702 | 1.0689 | 1.0694 | 2025-01-01 | 2025-12-31 23:00
2297 | WAINWRI9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0702 | 1.0612 | 1.067 | 2025-01-01 | 2025-12-31 23:00
1241 | LONGLK1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0701 | 1.0688 | 1.0693 | 2025-01-01 | 2025-12-31 23:00
557007 | BLACKFAGAS | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0701 | 1.0581 | 1.0678 | 2025-01-01 | 2025-12-31 23:00
557114 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0701 | 1.0581 | 1.0678 | 2025-01-01 | 2025-12-31 23:00
16351 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.07 | 1.07 | 1.07 | 2025-01-01 | 2025-12-31 23:00
1475 | OYEN 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0699 | 1.0642 | 1.0671 | 2025-01-01 | 2025-12-31 23:00
1046 | 7LA183TP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0698 | 1.0675 | 1.0684 | 2025-01-01 | 2025-12-31 23:00
1292 | MEAD_144 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0697 | 1.0675 | 1.0684 | 2025-01-01 | 2025-12-31 23:00
862 | PV-TAP7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0694 | 1.056 | 1.0643 | 2025-01-01 | 2025-12-31 23:00
1479 | AEC TAP | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0694 | 1.0606 | 1.0657 | 2025-01-01 | 2025-12-31 23:00
1289 | JACKPINE | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.067 | 1.0682 | 2025-01-01 | 2025-12-31 23:00
1609 | LIVOC500 | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.0648 | 1.0665 | 2025-01-01 | 2025-12-31 23:00
1747 | WT_G1 13.800 |  | 19 | PEACE RI |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.0632 | 1.0674 | 2025-01-01 | 2025-12-31 23:00
3747 | WT_G2 13.800 |  | 19 | PEACE RI |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.0632 | 1.0674 | 2025-01-01 | 2025-12-31 23:00
4747 | WT_G3 13.800 |  | 19 | PEACE RI |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.0632 | 1.0674 | 2025-01-01 | 2025-12-31 23:00
5747 | WT_G4 13.800 |  | 19 | PEACE RI |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0693 | 1.0632 | 1.0674 | 2025-01-01 | 2025-12-31 23:00
1686 | DOGRIB01 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0692 | 1.0674 | 1.0683 | 2025-01-01 | 2025-12-31 23:00
1464 | HEISLER7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.069 | 1.0595 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
1007 | HEIS_TP8 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0689 | 1.0594 | 1.0652 | 2025-01-01 | 2025-12-31 23:00
18080 | WESLY C8 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0687 | 1.0625 | 1.0668 | 2025-01-01 | 2025-12-31 23:00
19080 | WESLY C9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0686 | 1.0625 | 1.0668 | 2025-01-01 | 2025-12-31 23:00
1314 | BRIKER1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0685 | 1.055 | 1.0634 | 2025-01-01 | 2025-12-31 23:00
16201 | RUTHLK10 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0685 | 1.0673 | 1.0679 | 2025-01-01 | 2025-12-31 23:00
1465 | CORONAT8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.068 | 1.0509 | 1.0597 | 2025-01-01 | 2025-12-31 23:00
1409 | QUIGL1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0679 | 1.0656 | 1.0665 | 2025-01-01 | 2025-12-31 23:00
4132 | SUNDANL9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0679 | 1.0597 | 1.063 | 2025-01-01 | 2025-12-31 23:00
16020 | HIGH LV6 | 15 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0678 | 1.0636 | 1.065 | 2025-01-01 | 2025-12-31 23:00
1222 | PARS CR7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0677 | 1.0657 | 1.0666 | 2025-01-01 | 2025-12-31 23:00
1404 | CASTOR 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0677 | 1.0552 | 1.0613 | 2025-01-01 | 2025-12-31 23:00
1407 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0677 | 1.0552 | 1.0613 | 2025-01-01 | 2025-12-31 23:00
3107 | SUNDREA9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0677 | 1.0501 | 1.0632 | 2025-01-01 | 2025-12-31 23:00
1160 | BEZANSON | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0676 | 1.0542 | 1.0653 | 2025-01-01 | 2025-12-31 23:00
1290 | HORSERV7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0671 | 1.0634 | 1.0649 | 2025-01-01 | 2025-12-31 23:00
1480 | AEC EXP | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0669 | 1.058 | 1.0631 | 2025-01-01 | 2025-12-31 23:00
133 | WABAMUN4 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0668 | 1.0581 | 1.0616 | 2025-01-01 | 2025-12-31 23:00
1623 | ENGSTRM1 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0668 | 1.0645 | 1.0654 | 2025-01-01 | 2025-12-31 23:00
1419 | PEMUKN1 | 240 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0665 | 1.0652 | 1.0656 | 2025-01-01 | 2025-12-31 23:00
1683 | KEARL13A | 13.8 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0657 | 1.0591 | 1.0636 | 2025-01-01 | 2025-12-31 23:00
1696 | KEARL72D | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0657 | 1.0593 | 1.0637 | 2025-01-01 | 2025-12-31 23:00
18044 | KEMP RA9 | 4.16 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0657 | 1.0624 | 1.0645 | 2025-01-01 | 2025-12-31 23:00
558116 | MOWATG2 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0656 | 1.0656 | 1.0656 | 2025-01-01 | 2025-12-31 23:00
1478 | RICHDAL8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0651 | 1.0547 | 1.0611 | 2025-01-01 | 2025-12-31 23:00
1117 | CLAIR L | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0648 | 1.0505 | 1.0624 | 2025-01-01 | 2025-12-31 23:00
421 | KEEPHIL5 | 240 |  |  |  |  | 5215 | 5215 | 5214 | 0 | High | 1.0643 | 1.05 | 1.0558 | 2025-01-01 | 2025-12-31 23:00
21 | WESGEN 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0642 | 1.0569 | 1.0604 | 2025-01-01 | 2025-12-31 23:00
1022 | BLUMNOR7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0641 | 1.0641 | 1.0641 | 2025-01-01 | 2025-12-31 23:00
1408 | HANNA 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0626 | 1.0511 | 1.0582 | 2025-01-01 | 2025-12-31 23:00
10688 | EDD56-2 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0622 | 1.0616 | 1.0619 | 2025-01-01 | 2025-12-31 23:00
1239 | GREGOIRE | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0617 | 1.0593 | 1.0602 | 2025-01-01 | 2025-12-31 23:00
1025 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0616 | 1.0592 | 1.0601 | 2025-01-01 | 2025-12-31 23:00
1043 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.0616 | 1.0592 | 1.0601 | 2025-01-01 | 2025-12-31 23:00
1282 | WILO LK7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0616 | 1.0592 | 1.0601 | 2025-01-01 | 2025-12-31 23:00
1144 | DOME CU7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0614 | 1.0509 | 1.0597 | 2025-01-01 | 2025-12-31 23:00
144 | ALGAR 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0613 | 1.0584 | 1.0596 | 2025-01-01 | 2025-12-31 23:00
1170 | SIMONET7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0613 | 1.0588 | 1.0609 | 2025-01-01 | 2025-12-31 23:00
1625 | DAWES138 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0611 | 1.0583 | 1.0595 | 2025-01-01 | 2025-12-31 23:00
1267 | SARAH L8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0602 | 1.0528 | 1.0576 | 2025-01-01 | 2025-12-31 23:00
454 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.06 | 1.06 | 1.06 | 2025-01-01 | 2025-12-31 23:00
3248 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.06 | 1.06 | 1.06 | 2025-01-01 | 2025-12-31 23:00
3357 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.06 | 1.06 | 1.06 | 2025-01-01 | 2025-12-31 23:00
13236 | MUSKEG7 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.06 | 1.0589 | 1.0594 | 2025-01-01 | 2025-12-31 23:00
17351 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.06 | 1.06 | 1.06 | 2025-01-01 | 2025-12-31 23:00
1256 | SWEETHE7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0598 | 1.057 | 1.0582 | 2025-01-01 | 2025-12-31 23:00
19438 | LANFIN5 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0598 | 1.054 | 1.0571 | 2025-01-01 | 2025-12-31 23:00
1459 | EXCEL7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0595 | 1.0537 | 1.0568 | 2025-01-01 | 2025-12-31 23:00
4082 | CHEVRON9 | 13.8 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0595 | 1.0511 | 1.055 | 2025-01-01 | 2025-12-31 23:00
19070 | CRANBER9 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0591 | 1.0591 | 1.0591 | 2025-01-01 | 2025-12-31 23:00
1601 | THICKWD1 | 500 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0589 | 1.0563 | 1.0572 | 2025-01-01 | 2025-12-31 23:00
1474 | OYEN 7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0586 | 1.0511 | 1.0552 | 2025-01-01 | 2025-12-31 23:00
16 | FLATBUS7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0585 | 1.0518 | 1.0551 | 2025-01-01 | 2025-12-31 23:00
19 | WESGEN T | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0582 | 1.0514 | 1.0547 | 2025-01-01 | 2025-12-31 23:00
18302 | [6 empty] | 5215 | 5215 | 5215 | 0 | High | 1.058 | 1.058 | 1.058 | 2025-01-01 | 2025-12-31 23:00
1108 | EUREKA 8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0579 | 1.0533 | 1.0568 | 2025-01-01 | 2025-12-31 23:00
3380 | 539S_25_D6 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0579 | 1.0517 | 1.0547 | 2025-01-01 | 2025-12-31 23:00
44 | FT ASBN7 | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0576 | 1.0513 | 1.0548 | 2025-01-01 | 2025-12-31 23:00
844 | ASBNE TP | 138 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0576 | 1.0513 | 1.0548 | 2025-01-01 | 2025-12-31 23:00
3379 | 539S_25_D5 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0576 | 1.0514 | 1.0544 | 2025-01-01 | 2025-12-31 23:00
12249 | LNGLKCG2 13.800 |  | 25 | FORT MCM | 25 | Northeast | 5215 | 5215 | 5215 | 0 | High | 1.057 | 1.057 | 1.057 | 2025-01-01 | 2025-12-31 23:00
2301 | FOSTERCK | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0568 | 1.0553 | 1.0561 | 2025-01-01 | 2025-12-31 23:00
4249 | 878S-T | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0566 | 1.0566 | 1.0566 | 2025-01-01 | 2025-12-31 23:00
1106 | FRIEDEN8 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0565 | 1.0523 | 1.0555 | 2025-01-01 | 2025-12-31 23:00
1265 | HORUP4 | 34 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0542 | 1.0522 | 1.0532 | 2025-01-01 | 2025-12-31 23:00
1257 | EDD34T2 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.053 | 1.0524 | 1.0527 | 2025-01-01 | 2025-12-31 23:00
1259 | HORUP3 | 34 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.053 | 1.0506 | 1.0518 | 2025-01-01 | 2025-12-31 23:00
2259 | HORUP22 | 34 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0528 | 1.0504 | 1.0516 | 2025-01-01 | 2025-12-31 23:00
14351 | 942SD3 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0524 | 1.0503 | 1.0514 | 2025-01-01 | 2025-12-31 23:00
3334 | 29EDD55A | 13.8 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0518 | 1.0513 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
1264 | HORUP2 | 34 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0516 | 1.0506 | 1.0511 | 2025-01-01 | 2025-12-31 23:00
1204 | SYNC_D08 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0514 | 1.051 | 1.0512 | 2025-01-01 | 2025-12-31 23:00
1209 | SYNCRU_B | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0513 | 1.0509 | 1.0511 | 2025-01-01 | 2025-12-31 23:00
1210 | SYNCRU_A | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0513 | 1.051 | 1.0511 | 2025-01-01 | 2025-12-31 23:00
2264 | HORUP21 | 34 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0512 | 1.0502 | 1.0507 | 2025-01-01 | 2025-12-31 23:00
1233 | SYNC_UE1 | 69 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0505 | 1.0502 | 1.0503 | 2025-01-01 | 2025-12-31 23:00
19020 | HGHLVL/1 | 25 |  |  |  |  | 5215 | 5215 | 5215 | 0 | High | 1.0503 | 1.0503 | 1.0503 | 2025-01-01 | 2025-12-31 23:00
3272 | [6 empty] | 5215 | 5215 | 0 | 5215 | Low | 0.9443 | 0.8971 | 0.9293 | 2025-01-01 | 2025-12-31 23:00
549017 | MHS-3B | 138 |  |  |  |  | 5215 | 5215 | 0 | 5215 | Low | 0.9391 | 0.9333 | 0.93669 | 2025-01-01 | 2025-12-31 23:00
4280 | STIRLIN9 | 25 |  |  |  |  | 5215 | 5215 | 0 | 5215 | Low | 0.9328 | 0.9136 | 0.92201 | 2025-01-01 | 2025-12-31 23:00
549016 | MHS-3A | 138 |  |  |  |  | 5215 | 5215 | 0 | 5215 | Low | 0.9226 | 0.9166 | 0.9201 | 2025-01-01 | 2025-12-31 23:00
61994 | [6 empty] | 5215 | 5215 | 0 | 5215 | Low | 0.9116 | 0.8965 | 0.89975 | 2025-01-01 | 2025-12-31 23:00
62994 | [6 empty] | 5215 | 5215 | 0 | 5215 | Low | 0.9116 | 0.8965 | 0.89975 | 2025-01-01 | 2025-12-31 23:00
64435 | HALKRIK8 | 0.48 |  |  |  |  | 5215 | 5215 | 0 | 5215 | Low | 0.8946 | 0.885 | 0.89141 | 2025-01-01 | 2025-12-31 23:00
65435 | HALKRIK7 | 0.48 |  |  |  |  | 5215 | 5215 | 0 | 5215 | Low | 0.8946 | 0.885 | 0.89141 | 2025-01-01 | 2025-12-31 23:00
2359 | HORUP23 | 34 |  |  |  |  | 5214 | 5214 | 5211 | 0 | High | 1.0524 | 1.05 | 1.0512 | 2025-01-01 | 2025-12-31 23:00
1422 | NEVIS 4 | 240 |  |  |  |  | 5213 | 5213 | 5213 | 0 | High | 1.0628 | 1.0501 | 1.0593 | 2025-01-01 | 2025-12-31 23:00
150 | WILLESD4 | 240 |  |  |  |  | 5213 | 5213 | 5213 | 0 | High | 1.0607 | 1.0503 | 1.0566 | 2025-01-01 | 2025-12-31 23:00
995 | W.GRN TP | 240 |  |  |  |  | 5213 | 5213 | 5213 | 0 | High | 1.0607 | 1.0503 | 1.0566 | 2025-01-01 | 2025-12-31 23:00
153 | BRAZEAU4 | 240 |  |  |  |  | 5213 | 5213 | 5213 | 0 | High | 1.0595 | 1.0501 | 1.0544 | 2025-01-01 | 2025-12-31 23:00
1383 | VERMILO7 | 138 |  |  |  |  | 5210 | 5210 | 5210 | 0 | High | 1.069 | 1.0502 | 1.0632 | 2025-01-01 | 2025-12-31 23:00
308 | FLATLK-2 | 138 |  |  |  |  | 5210 | 5210 | 5209 | 0 | High | 1.0559 | 1.05 | 1.0533 | 2025-01-01 | 2025-12-31 23:00
637 | ALPACTAP | 138 |  |  |  |  | 5210 | 5210 | 5209 | 0 | High | 1.0559 | 1.05 | 1.0533 | 2025-01-01 | 2025-12-31 23:00
1324 | 7LA65_TP | 138 |  |  |  |  | 5209 | 5209 | 5209 | 0 | High | 1.0689 | 1.0501 | 1.063 | 2025-01-01 | 2025-12-31 23:00
19351 | 942SD2 | 13.8 |  |  |  |  | 5209 | 5209 | 5206 | 0 | High | 1.052 | 1.05 | 1.0511 | 2025-01-01 | 2025-12-31 23:00
873 | RATTLESNK | 138 |  |  |  |  | 5207 | 5207 | 5207 | 0 | High | 1.096 | 1.0501 | 1.0773 | 2025-01-01 | 2025-12-31 23:00
875 | 879AL_TAP | 138 |  |  |  |  | 5207 | 5207 | 5206 | 0 | High | 1.0959 | 1.05 | 1.0772 | 2025-01-01 | 2025-12-31 23:00
155 | BENALTO4 | 240 |  |  |  |  | 5196 | 5196 | 5195 | 0 | High | 1.0603 | 1.05 | 1.0567 | 2025-01-01 | 2025-12-31 23:00
1322 | NORG_TP | 138 |  |  |  |  | 5195 | 5195 | 5194 | 0 | High | 1.0605 | 1.05 | 1.0566 | 2025-01-01 | 2025-12-31 23:00
1047 | DRURY138 | 138 |  |  |  |  | 5194 | 5194 | 5194 | 0 | High | 1.0681 | 1.0502 | 1.062 | 2025-01-01 | 2025-12-31 23:00
4094 | ERVICK 9 | 25 |  |  |  |  | 5193 | 5193 | 5193 | 0 | High | 1.0631 | 1.0501 | 1.057 | 2025-01-01 | 2025-12-31 23:00
1340 | NORB01 | 138 |  |  |  |  | 5193 | 5193 | 5192 | 0 | High | 1.0603 | 1.05 | 1.0564 | 2025-01-01 | 2025-12-31 23:00
3159 | LANGDOA9 | 20 |  |  |  |  | 5189 | 5189 | 5188 | 0 | High | 1.2242 | 1.05 | 1.1691 | 2025-01-01 | 2025-12-31 23:00
4159 | LANGDON9 | 20 |  |  |  |  | 5188 | 5188 | 5188 | 0 | High | 1.2261 | 1.0501 | 1.1704 | 2025-01-01 | 2025-12-31 23:00
1110 | MERC TAP | 138 |  |  |  |  | 5174 | 5174 | 5173 | 0 | High | 1.0642 | 1.05 | 1.0618 | 2025-01-01 | 2025-12-31 23:00
203 | SARCEE C | 13.8 |  |  |  |  | 5172 | 5172 | 5172 | 0 | High | 1.0782 | 1.0522 | 1.0656 | 2025-01-01 | 2025-12-31 23:00
29202 | SARCEE C | 13.8 |  |  |  |  | 5172 | 5172 | 5172 | 0 | High | 1.0782 | 1.0522 | 1.0656 | 2025-01-01 | 2025-12-31 23:00
1121 | CRYST L7 | 138 |  |  |  |  | 5170 | 5170 | 5170 | 0 | High | 1.0655 | 1.0503 | 1.063 | 2025-01-01 | 2025-12-31 23:00
1103 | THORN_144 | 138 |  |  |  |  | 5167 | 5167 | 5167 | 0 | High | 1.0607 | 1.0501 | 1.0589 | 2025-01-01 | 2025-12-31 23:00
76 | IPPL ST7 | 138 |  |  |  |  | 5163 | 5163 | 5160 | 0 | High | 1.0603 | 1.05 | 1.056 | 2025-01-01 | 2025-12-31 23:00
1143 | BIG MTN7 | 138 |  |  |  |  | 5161 | 5161 | 5161 | 0 | High | 1.0646 | 1.0501 | 1.0619 | 2025-01-01 | 2025-12-31 23:00
1145 | BRDGE C7 | 138 |  |  |  |  | 5161 | 5161 | 5161 | 0 | High | 1.0646 | 1.0503 | 1.0619 | 2025-01-01 | 2025-12-31 23:00
1109 | MERCER 7 | 138 |  |  |  |  | 5161 | 5161 | 5160 | 0 | High | 1.062 | 1.05 | 1.0596 | 2025-01-01 | 2025-12-31 23:00
1119 | GOODFAR7 | 138 |  |  |  |  | 5160 | 5160 | 5160 | 0 | High | 1.0639 | 1.0501 | 1.0611 | 2025-01-01 | 2025-12-31 23:00
825 | CGETAP | 138 |  |  |  |  | 5159 | 5159 | 5159 | 0 | High | 1.0636 | 1.0501 | 1.0609 | 2025-01-01 | 2025-12-31 23:00
1101 | GPEP7 | 138 |  |  |  |  | 5159 | 5159 | 5159 | 0 | High | 1.0636 | 1.0501 | 1.0609 | 2025-01-01 | 2025-12-31 23:00
1146 | P&G 8 13.800 |  | 20 | GRANDE P | 20 | Northwest | 5157 | 5157 | 5157 | 0 | High | 1.0683 | 1.0507 | 1.0649 | 2025-01-01 | 2025-12-31 23:00
5159 | 102ST4 | 240 |  |  |  |  | 5156 | 5156 | 5155 | 0 | High | 1.1812 | 1.05 | 1.1385 | 2025-01-01 | 2025-12-31 23:00
1126 | FLYINGS7 | 138 |  |  |  |  | 5155 | 5155 | 5155 | 0 | High | 1.0619 | 1.0502 | 1.0592 | 2025-01-01 | 2025-12-31 23:00
1137 | AWTAP | 138 |  |  |  |  | 5148 | 5148 | 5148 | 0 | High | 1.0624 | 1.0502 | 1.0595 | 2025-01-01 | 2025-12-31 23:00
1139 | ALBRIGHT | 138 |  |  |  |  | 5148 | 5148 | 5148 | 0 | High | 1.0623 | 1.0501 | 1.0595 | 2025-01-01 | 2025-12-31 23:00
1142 | BEARCK1 | 138 |  |  |  |  | 5142 | 5142 | 5141 | 0 | High | 1.0622 | 1.05 | 1.0593 | 2025-01-01 | 2025-12-31 23:00
2340 | [6 empty] | 5142 | 5142 | 5141 | 0 | High | 1.057 | 1.05 | 1.0552 | 2025-01-01 | 2025-12-31 23:00
1138 | BCTAP | 138 |  |  |  |  | 5140 | 5140 | 5139 | 0 | High | 1.0621 | 1.05 | 1.0592 | 2025-01-01 | 2025-12-31 23:00
1140 | P&G 7 | 138 |  |  |  |  | 5135 | 5135 | 5134 | 0 | High | 1.0619 | 1.05 | 1.0591 | 2025-01-01 | 2025-12-31 23:00
380 | RUNDLE 9 | 25 |  |  |  |  | 5119 | 5119 | 5106 | 0 | High | 1.0654 | 1.05 | 1.0561 | 2025-01-01 | 2025-12-31 23:00
990001 | [6 empty] | 5113 | 5113 | 5106 | 0 | High | 1.0742 | 1.05 | 1.0621 | 2025-01-01 | 2025-12-31 23:00
18307 | [6 empty] | 5095 | 5095 | 5095 | 0 | High | 1.0533 | 1.0508 | 1.0521 | 2025-01-01 | 2025-12-31 23:00
19307 |  | 25 |  |  |  |  | 5095 | 5095 | 5095 | 0 | High | 1.0533 | 1.0508 | 1.0521 | 2025-01-01 | 2025-12-31 23:00
2459 | HORUP17 13.800 |  | 25 | FORT MCM |  |  | 5042 | 5042 | 5000 | 0 | High | 1.0519 | 1.05 | 1.0507 | 2025-01-01 01:00 | 2025-12-31 23:00
430 | W BROOK4 | 240 |  |  |  |  | 5038 | 5038 | 5025 | 0 | High | 1.0604 | 1.05 | 1.0539 | 2025-01-01 | 2025-12-31 23:00
379 | THREE A9 | 25 |  |  |  |  | 5032 | 5032 | 5024 | 0 | High | 1.065 | 1.05 | 1.0558 | 2025-01-01 | 2025-12-31 23:00
918 | CASS01 | 240 |  |  |  |  | 5027 | 5027 | 5021 | 0 | High | 1.0604 | 1.05 | 1.0539 | 2025-01-01 | 2025-12-31 23:00
4242 | HIGH RI9 | 25 |  |  |  |  | 5010 | 5010 | 5003 | 0 | High | 1.0702 | 1.05 | 1.0562 | 2025-01-01 | 2025-12-31 23:00
557277 | [6 empty] | 4915 | 4915 | 4907 | 0 | High | 1.0721 | 1.05 | 1.0604 | 2025-01-01 | 2025-12-31 23:00
1118 | POPLAR 7 | 138 |  |  |  |  | 4859 | 4859 | 4834 | 0 | High | 1.0589 | 1.05 | 1.0567 | 2025-01-01 | 2025-12-31 23:00
1120 | LOWE1 | 138 |  |  |  |  | 4859 | 4859 | 4833 | 0 | High | 1.0589 | 1.05 | 1.0567 | 2025-01-01 | 2025-12-31 23:00
4277 | WESTFIE9 | 25 |  |  |  |  | 4842 | 4842 | 4835 | 0 | High | 1.0709 | 1.05 | 1.0598 | 2025-01-01 | 2025-12-31 23:00
4272 | TABER 9 | 25 |  |  |  |  | 4826 | 4826 | 4821 | 0 | High | 1.068 | 1.05 | 1.0572 | 2025-01-01 | 2025-12-31 23:00
895 | 515S TAP | 69 |  |  |  |  | 4725 | 4725 | 4696 | 0 | High | 1.0536 | 1.05 | 1.0514 | 2025-01-01 | 2025-12-31 23:00
2242 | HIGH RA9 | 25 |  |  |  |  | 4700 | 4700 | 4685 | 0 | High | 1.071 | 1.05 | 1.0551 | 2025-01-01 | 2025-12-31 23:00
18383 | VERMILA8 | 25 |  |  |  |  | 4662 | 4662 | 4644 | 0 | High | 1.0602 | 1.05 | 1.0551 | 2025-01-01 03:00 | 2025-12-31 23:00
54 | [6 empty] | 4595 | 4595 | 4534 | 0 | High | 1.0568 | 1.05 | 1.0516 | 2025-01-01 | 2025-12-31 23:00
4400 | MONARCH9 | 25 |  |  |  |  | 4545 | 4545 | 4534 | 0 | High | 1.067 | 1.05 | 1.0576 | 2025-01-01 02:00 | 2025-12-31 23:00
1012 | NEWELL2 | 240 |  |  |  |  | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
1618 | [6 empty] | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
1620 | [6 empty] | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
1621 | [6 empty] | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
76002 | [6 empty] | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
76502 | B23S_01_2 | 34.5 |  |  |  |  | 4525 | 4525 | 4498 | 0 | High | 1.0594 | 1.05 | 1.0529 | 2025-01-01 | 2025-12-31 23:00
19105 | FRIEDEN9 | 25 |  |  |  |  | 4514 | 4514 | 4481 | 0 | High | 1.0519 | 1.05 | 1.051 | 2025-01-01 | 2025-12-31 23:00
1134 | ELMWORT7 | 138 |  |  |  |  | 4498 | 4498 | 4493 | 0 | High | 1.0583 | 1.05 | 1.0565 | 2025-01-01 | 2025-12-31 23:00
417 | WAUP1 | 138 |  |  |  |  | 4496 | 4496 | 4445 | 0 | High | 1.0536 | 1.05 | 1.0512 | 2025-01-01 01:00 | 2025-12-31 23:00
1132 | WAP JCT7 | 138 |  |  |  |  | 4471 | 4471 | 4466 | 0 | High | 1.0579 | 1.05 | 1.0562 | 2025-01-01 | 2025-12-31 23:00
1123 | SADHL TP | 138 |  |  |  |  | 4449 | 4449 | 4449 | 0 | High | 1.0572 | 1.0502 | 1.0556 | 2025-01-01 | 2025-12-31 23:00
1114 | UPDIKE1 | 138 |  |  |  |  | 4445 | 4445 | 4444 | 0 | High | 1.0565 | 1.05 | 1.0548 | 2025-01-01 | 2025-12-31 23:00
6 | [6 empty] | 4362 | 4362 | 4354 | 0 | High | 1.0915 | 1.05 | 1.0575 | 2025-01-01 | 2025-12-31 23:00
3121 | OLDS A9 | 25 |  |  |  |  | 4346 | 4346 | 4334 | 0 | High | 1.0664 | 1.05 | 1.0543 | 2025-01-01 | 2025-12-31 23:00
18687 | BOHN9 | 4.16 |  |  |  |  | 4293 | 4293 | 4186 | 0 | High | 1.0533 | 1.05 | 1.0508 | 2025-01-01 | 2025-12-31 23:00
4006 | DICKSON9 | 25 |  |  |  |  | 4182 | 4182 | 4171 | 0 | High | 1.0873 | 1.05 | 1.0564 | 2025-01-01 | 2025-12-31 23:00
1135 | WAPITI 7 | 138 |  |  |  |  | 4137 | 4137 | 4115 | 0 | High | 1.053 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
560 | ENMX13S8 | 69 |  |  |  |  | 4109 | 4109 | 4095 | 0 | High | 1.0639 | 1.05 | 1.0537 | 2025-01-01 | 2025-12-31 23:00
156 | E CROSS4 | 240 |  |  |  |  | 4044 | 4044 | 4026 | 0 | High | 1.0566 | 1.05 | 1.0544 | 2025-01-01 | 2025-12-31 23:00
988 | [6 empty] | 4044 | 4044 | 4026 | 0 | High | 1.0566 | 1.05 | 1.0544 | 2025-01-01 | 2025-12-31 23:00
4286 | ENCHANT9 | 25 |  |  |  |  | 3980 | 3980 | 3977 | 0 | High | 1.0629 | 1.05 | 1.0574 | 2025-01-01 | 2025-12-31 23:00
1449 | MICH. C8 | 69 |  |  |  |  | 3978 | 3978 | 3978 | 0 | High | 1.058 | 1.0524 | 1.0568 | 2025-01-01 | 2025-12-31 21:00
160 | JANET 4 | 240 |  |  |  |  | 3977 | 3977 | 3972 | 0 | High | 1.057 | 1.05 | 1.0555 | 2025-01-01 | 2025-12-31 23:00
75003 | [6 empty] | 3977 | 3977 | 3972 | 0 | High | 1.057 | 1.05 | 1.0555 | 2025-01-01 | 2025-12-31 23:00
75503 | [6 empty] | 3977 | 3977 | 3972 | 0 | High | 1.057 | 1.05 | 1.0555 | 2025-01-01 | 2025-12-31 23:00
420 | KEEPHIL4 | 240 |  |  |  |  | 3864 | 3864 | 3800 | 0 | High | 1.0557 | 1.05 | 1.0514 | 2025-01-01 | 2025-12-31 23:00
766 | BAUERTAP | 138 |  |  |  |  | 3824 | 3824 | 3788 | 0 | High | 1.0568 | 1.05 | 1.0529 | 2025-01-03 14:00 | 2025-12-31 23:00
772 | ENMX25S7 | 240 |  |  |  |  | 3820 | 3820 | 3814 | 0 | High | 1.0556 | 1.05 | 1.0542 | 2025-01-01 | 2025-12-31 23:00
1113 | BAUER1 | 138 |  |  |  |  | 3815 | 3815 | 3782 | 0 | High | 1.0568 | 1.05 | 1.0528 | 2025-01-03 14:00 | 2025-12-31 23:00
557120 | [6 empty] | 3758 | 3758 | 449 | 3303 | Low | 1.0563 | 0.6625 | 0.90544 | 2025-01-01 | 2025-12-31 23:00
4485 | [6 empty] | 3738 | 3738 | 3735 | 0 | High | 1.054 | 1.05 | 1.0538 | 2025-01-01 | 2025-12-31 23:00
19478 | [6 empty] | 3707 | 3707 | 3691 | 0 | High | 1.054 | 1.05 | 1.0518 | 2025-01-01 | 2025-12-31 20:00
2401 | [6 empty] | 3638 | 3638 | 3637 | 0 | High | 1.1135 | 1.05 | 1.102 | 2025-01-01 | 2025-12-31 23:00
159 | LANGDON4 | 240 |  |  |  |  | 3572 | 3572 | 3571 | 0 | High | 1.054 | 1.05 | 1.0538 | 2025-01-01 | 2025-12-31 23:00
485 | [6 empty] | 3572 | 3572 | 3571 | 0 | High | 1.054 | 1.05 | 1.0538 | 2025-01-01 | 2025-12-31 23:00
25298 | [6 empty] | 3542 | 3542 | 3502 | 0 | High | 1.0568 | 1.05 | 1.0518 | 2025-01-01 | 2025-12-31 23:00
1488 | MANNIX 8 | 69 |  |  |  |  | 3486 | 3486 | 3412 | 0 | High | 1.0558 | 1.05 | 1.0513 | 2025-01-01 03:00 | 2025-12-31 23:00
544 | ENMX65S4 | 240 |  |  |  |  | 3471 | 3471 | 3463 | 0 | High | 1.0533 | 1.05 | 1.0518 | 2025-01-01 | 2025-12-31 23:00
480 | BENNETTS | 240 |  |  |  |  | 3333 | 3333 | 3331 | 0 | High | 1.0547 | 1.05 | 1.0527 | 2025-01-01 | 2025-12-31 23:00
549026 | TRAVERS_4 | 240 |  |  |  |  | 3233 | 3233 | 3189 | 0 | High | 1.0559 | 1.05 | 1.0514 | 2025-01-01 | 2025-12-31 23:00
547026 | TRAVERS_5 | 240 |  |  |  |  | 3217 | 3217 | 3163 | 0 | High | 1.0559 | 1.05 | 1.0514 | 2025-01-01 | 2025-12-31 23:00
560014 | BCDG2 | 25 |  |  |  |  | 3067 | 3067 | 3065 | 0 | High | 1.1294 | 1.05 | 1.0868 | 2025-01-01 | 2025-12-31
669 | BOWMAN1 | 240 |  |  |  |  | 3021 | 3021 | 2991 | 0 | High | 1.0547 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
75005 | [6 empty] | 3021 | 3021 | 2990 | 0 | High | 1.0547 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
75006 | [6 empty] | 3021 | 3021 | 2990 | 0 | High | 1.0547 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
75505 | [6 empty] | 3021 | 3021 | 2991 | 0 | High | 1.0547 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
75506 | [6 empty] | 3021 | 3021 | 2991 | 0 | High | 1.0547 | 1.05 | 1.0515 | 2025-01-01 | 2025-12-31 23:00
4344 | [6 empty] | 3019 | 3019 | 2919 | 0 | High | 1.052 | 1.05 | 1.0508 | 2025-01-01 01:00 | 2025-12-31 23:00
1363 | VINCENT8 | 138 |  |  |  |  | 2951 | 2951 | 2921 | 0 | High | 1.0554 | 1.05 | 1.052 | 2025-01-07 05:00 | 2025-12-31 23:00
560013 | BCDG1 | 25 |  |  |  |  | 2813 | 2813 | 2811 | 0 | High | 1.1072 | 1.05 | 1.0813 | 2025-01-01 | 2025-12-30 07:00
943 | [6 empty] | 2560 | 2560 | 2492 | 0 | High | 1.0553 | 1.05 | 1.051 | 2025-01-01 | 2025-12-31 23:00
554401 | [6 empty] | 2503 | 2503 | 2488 | 0 | High | 1.0583 | 1.05 | 1.0524 | 2025-01-01 | 2025-12-31 23:00
4098 | RIMBEY 9 | 25 |  |  |  |  | 2464 | 2464 | 2372 | 0 | High | 1.0547 | 1.05 | 1.0507 | 2025-01-01 01:00 | 2025-12-31 23:00
4271 | BULLS H9 | 25 |  |  |  |  | 2415 | 2415 | 2328 | 0 | High | 1.052 | 1.05 | 1.0507 | 2025-01-01 | 2025-12-31 23:00
3284 | BUTTE8 | 25 |  |  |  |  | 2411 | 2411 | 2321 | 0 | High | 1.052 | 1.05 | 1.0507 | 2025-01-01 | 2025-12-31 23:00
516 | [6 empty] | 2280 | 2280 | 2221 | 0 | High | 1.0601 | 1.05 | 1.0514 | 2025-01-01 01:00 | 2025-12-31 23:00
550004 | [6 empty] | 2278 | 2278 | 2275 | 0 | High | 1.1295 | 1.05 | 1.0894 | 2025-01-03 12:00 | 2025-12-30 20:00
1504 | [6 empty] | 2101 | 2101 | 0 | 2099 | Low | 0.95 | 0.7608 | 0.92662 | 2025-01-07 11:00 | 2025-12-31 22:00
818 | [6 empty] | 2053 | 2053 | 0 | 2049 | Low | 0.95 | 0.7617 | 0.92682 | 2025-01-07 11:00 | 2025-12-31 22:00
1506 | [6 empty] | 2048 | 2048 | 0 | 2045 | Low | 0.95 | 0.7608 | 0.92671 | 2025-01-07 11:00 | 2025-12-31 22:00
817 | [6 empty] | 2036 | 2036 | 0 | 2035 | Low | 0.95 | 0.7611 | 0.92681 | 2025-01-07 11:00 | 2025-12-31 22:00
25299 | [6 empty] | 1987 | 1987 | 1938 | 0 | High | 1.0563 | 1.05 | 1.0513 | 2025-01-01 01:00 | 2025-12-31 23:00
1505 | [6 empty] | 1801 | 1801 | 0 | 1799 | Low | 0.95 | 0.7927 | 0.93225 | 2025-01-07 11:00 | 2025-12-31 22:00
2399 | [6 empty] | 1782 | 1782 | 1766 | 0 | High | 1.054 | 1.05 | 1.0524 | 2025-01-01 02:00 | 2025-12-31 22:00
4231 | [6 empty] | 1781 | 1781 | 1756 | 0 | High | 1.0651 | 1.05 | 1.0522 | 2025-01-01 | 2025-12-28 05:00
819 | [6 empty] | 1718 | 1718 | 0 | 1714 | Low | 0.95 | 0.7947 | 0.93311 | 2025-01-07 11:00 | 2025-12-31 22:00
1472 | MONITOR8 | 69 |  |  |  |  | 1710 | 1710 | 1595 | 0 | High | 1.0512 | 1.05 | 1.0504 | 2025-01-07 10:00 | 2025-12-31
4692 | N LETHB9 | 25 |  |  |  |  | 1705 | 1705 | 1684 | 0 | High | 1.054 | 1.05 | 1.052 | 2025-01-01 09:00 | 2025-12-31 22:00
1503 | [6 empty] | 1629 | 1629 | 0 | 1628 | Low | 0.95 | 0.7565 | 0.92969 | 2025-01-07 11:00 | 2025-12-31 22:00
1498 | BIGFOOT8 | 69 |  |  |  |  | 1621 | 1621 | 1535 | 0 | High | 1.0549 | 1.05 | 1.0511 | 2025-01-07 05:00 | 2025-12-29 20:00
816 | [6 empty] | 1597 | 1597 | 0 | 1595 | Low | 0.95 | 0.7575 | 0.93007 | 2025-01-07 11:00 | 2025-12-31 22:00
3100 | [6 empty] | 1593 | 1593 | 1537 | 0 | High | 1.0537 | 1.05 | 1.051 | 2025-01-01 03:00 | 2025-12-31 23:00
1492 | BAT. RV8 | 69 |  |  |  |  | 1592 | 1592 | 1513 | 0 | High | 1.0548 | 1.05 | 1.0511 | 2025-01-07 05:00 | 2025-12-29 20:00
550003 | [6 empty] | 1562 | 1562 | 1560 | 0 | High | 1.0795 | 1.05 | 1.0651 | 2025-01-03 15:00 | 2025-12-30 07:00
4100 | [6 empty] | 1523 | 1523 | 1462 | 0 | High | 1.0536 | 1.05 | 1.0509 | 2025-01-01 03:00 | 2025-12-31 23:00
4366 | EMPRESS8 | 25 |  |  |  |  | 1404 | 1404 | 1338 | 0 | High | 1.052 | 1.05 | 1.0507 | 2025-01-01 | 2025-12-31 23:00
557316 | [6 empty] | 1404 | 1404 | 1338 | 0 | High | 1.052 | 1.05 | 1.0507 | 2025-01-01 | 2025-12-31 23:00
2690 | [6 empty] | 1400 | 1400 | 1355 | 0 | High | 1.052 | 1.05 | 1.0508 | 2025-01-01 | 2025-12-31 23:00
90000 | 1201L | 500 |  |  |  |  | 1325 | 1325 | 835 | 484 | High | 1.0772 | 0.7162 | 1.0149 | 2025-01-01 | 2025-12-31 21:00
1 | JUDY515S | 69 |  |  |  |  | 1284 | 1284 | 1152 | 0 | High | 1.0518 | 1.05 | 1.0504 | 2025-01-01 06:00 | 2025-12-31 21:00
19052 | HAMBURG9 | 25 |  |  |  |  | 1229 | 1229 | 926 | 0 | High | 1.0505 | 1.05 | 1.0501 | 2025-02-15 18:00 | 2025-11-30 09:00
1124 | [6 empty] | 1211 | 1211 | 1123 | 0 | High | 1.051 | 1.05 | 1.0503 | 2025-02-01 | 2025-12-31 07:00
783 | 1045L TAP | 240 |  |  |  |  | 1192 | 1192 | 1127 | 0 | High | 1.0539 | 1.05 | 1.0508 | 2025-01-01 02:00 | 2025-12-31 22:00
362 | EDGERTO7 | 138 |  |  |  |  | 1164 | 1164 | 1126 | 0 | High | 1.0524 | 1.05 | 1.0507 | 2025-01-07 10:00 | 2025-12-30 07:00
4266 | [6 empty] | 1119 | 1119 | 1100 | 0 | High | 1.052 | 1.05 | 1.051 | 2025-01-01 16:00 | 2025-12-31 21:00
557016 | [6 empty] | 1119 | 1119 | 1100 | 0 | High | 1.052 | 1.05 | 1.051 | 2025-01-01 16:00 | 2025-12-31 21:00
3264 | [6 empty] | 1119 | 1119 | 701 | 0 | High | 1.0504 | 1.05 | 1.0501 | 2025-01-02 05:00 | 2025-12-31 23:00
1501 | [6 empty] | 995 | 995 | 0 | 993 | Low | 0.95 | 0.7645 | 0.93517 | 2025-01-07 11:00 | 2025-12-31 21:00
1401 | [6 empty] | 963 | 963 | 926 | 0 | High | 1.0543 | 1.05 | 1.0512 | 2025-01-07 05:00 | 2025-12-26 12:00
704 | [6 empty] | 857 | 857 | 0 | 796 | Low | 0.95 | 0.9472 | 0.94946 | 2025-01-07 22:00 | 2025-12-31 18:00
3692 | [6 empty] | 839 | 839 | 804 | 0 | High | 1.052 | 1.05 | 1.0508 | 2025-01-01 | 2025-12-31 23:00
1507 | CRANBROO | 500 |  |  |  |  | 834 | 834 | 93 | 737 | Low | 1.056 | 0.7327 | 0.94705 | 2025-01-01 17:00 | 2025-12-31 21:00
269 | BURDETT7 | 138 |  |  |  |  | 786 | 786 | 774 | 0 | High | 1.055 | 1.05 | 1.0512 | 2025-01-01 10:00 | 2025-12-31 18:00
4120 | [6 empty] | 777 | 777 | 768 | 0 | High | 1.067 | 1.05 | 1.0528 | 2025-01-01 09:00 | 2025-12-28 19:00
599 | ENMX36S8 | 69 |  |  |  |  | 745 | 745 | 670 | 0 | High | 1.0603 | 1.05 | 1.0538 | 2025-01-01 09:00 | 2025-12-31 21:00
67873 | [6 empty] | 730 | 730 | 724 | 0 | High | 1.0575 | 1.05 | 1.0528 | 2025-01-07 17:00 | 2025-12-31 18:00
558120 | [6 empty] | 717 | 717 | 713 | 1 | High | 1.0565 | 0.9468 | 1.0524 | 2025-01-01 09:00 | 2025-12-26 13:00
4270 | [6 empty] | 691 | 691 | 660 | 0 | High | 1.0569 | 1.05 | 1.051 | 2025-01-01 09:00 | 2025-12-30 21:00
3120 | [6 empty] | 688 | 688 | 674 | 0 | High | 1.0591 | 1.05 | 1.0521 | 2025-01-01 12:00 | 2025-12-28 19:00
552447 | [6 empty] | 687 | 687 | 674 | 0 | High | 1.0511 | 1.05 | 1.0507 | 2025-01-01 15:00 | 2025-12-31 07:00
1350 | WHITBY 7 | 138 |  |  |  |  | 662 | 662 | 600 | 0 | High | 1.0521 | 1.05 | 1.0505 | 2025-01-07 11:00 | 2025-12-30 20:00
552449 | [6 empty] | 661 | 661 | 648 | 0 | High | 1.0511 | 1.05 | 1.0506 | 2025-01-01 15:00 | 2025-12-31 07:00
17134 | ELMWORT6 6.9000 |  | 20 | GRANDE P | 20 | Northwest | 645 | 645 | 637 | 0 | High | 1.0555 | 1.05 | 1.0514 | 2025-01-10 22:00 | 2025-12-25 06:00
25334 | [6 empty] | 605 | 605 | 586 | 0 | High | 1.053 | 1.05 | 1.051 | 2025-01-01 02:00 | 2025-12-31
4380 | 539S_13.8_G213.800 |  | 25 | FORT MCM | 25 | Northeast | 605 | 605 | 544 | 0 | High | 1.0521 | 1.05 | 1.0505 | 2025-01-01 03:00 | 2025-12-29 20:00
1107 | [6 empty] | 579 | 579 | 419 | 0 | High | 1.0505 | 1.05 | 1.0501 | 2025-01-08 06:00 | 2025-12-09 08:00
232 | [6 empty] | 570 | 570 | 0 | 567 | Low | 0.95 | 0.8117 | 0.94156 | 2025-01-07 11:00 | 2025-12-31 21:00
4209 | [6 empty] | 506 | 506 | 478 | 0 | High | 1.052 | 1.05 | 1.0507 | 2025-01-01 03:00 | 2025-12-30 22:00
4278 | [6 empty] | 501 | 501 | 486 | 0 | High | 1.052 | 1.05 | 1.051 | 2025-01-07 08:00 | 2025-12-24 14:00
456 | BENNETTP | 500 |  |  |  |  | 479 | 479 | 471 | 5 | High | 1.0607 | 0.8571 | 1.0523 | 2025-01-01 | 2025-12-27 23:00
25331 | [6 empty] | 466 | 466 | 450 | 0 | High | 1.0527 | 1.05 | 1.0509 | 2025-01-01 02:00 | 2025-12-30 20:00
214 | [6 empty] | 458 | 458 | 0 | 453 | Low | 0.95 | 0.8825 | 0.94686 | 2025-01-07 11:00 | 2025-12-31 21:00
18242 | KINOSIS4 | 25 |  |  |  |  | 456 | 456 | 389 | 0 | High | 1.0514 | 1.05 | 1.0503 | 2025-01-07 10:00 | 2025-12-29 20:00
4699 | [6 empty] | 452 | 452 | 446 | 0 | High | 1.0523 | 1.05 | 1.0511 | 2025-01-01 11:00 | 2025-12-31 19:00
3450 | [6 empty] | 436 | 436 | 0 | 417 | Low | 0.95 | 0.9457 | 0.94892 | 2025-02-04 06:00 | 2025-12-31 20:00
985 | [6 empty] | 430 | 430 | 411 | 0 | High | 1.0542 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
4086 | [6 empty] | 426 | 426 | 398 | 0 | High | 1.0519 | 1.05 | 1.0505 | 2025-01-07 16:00 | 2025-12-29 21:00
4035 | LODGEPO9 | 25 |  |  |  |  | 425 | 425 | 410 | 0 | High | 1.0539 | 1.05 | 1.0509 | 2025-01-03 18:00 | 2025-12-28 17:00
507 | ROSSDALE | 69 |  |  |  |  | 419 | 419 | 395 | 0 | High | 1.0548 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
580006 | [6 empty] | 419 | 419 | 395 | 0 | High | 1.0548 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
580007 | [6 empty] | 419 | 419 | 395 | 0 | High | 1.0548 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
580008 | [6 empty] | 419 | 419 | 395 | 0 | High | 1.0548 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
580009 | [6 empty] | 419 | 419 | 395 | 0 | High | 1.0548 | 1.05 | 1.0512 | 2025-01-01 03:00 | 2025-12-29 20:00
4099 | [6 empty] | 362 | 362 | 353 | 0 | High | 1.0532 | 1.05 | 1.0513 | 2025-01-07 13:00 | 2025-12-31 21:00
558 | [6 empty] | 339 | 339 | 339 | 0 | High | 1.057 | 1.0512 | 1.0547 | 2025-01-07 13:00 | 2025-12-31 21:00
553 | [6 empty] | 334 | 334 | 333 | 0 | High | 1.0552 | 1.05 | 1.053 | 2025-01-07 13:00 | 2025-12-31 21:00
528 | [6 empty] | 332 | 332 | 320 | 0 | High | 1.0575 | 1.05 | 1.0513 | 2025-01-01 03:00 | 2025-12-27 06:00
4017 | [6 empty] | 331 | 331 | 309 | 0 | High | 1.0517 | 1.05 | 1.0505 | 2025-01-01 06:00 | 2025-12-31 21:00
3180 | [6 empty] | 311 | 311 | 311 | 0 | High | 1.0539 | 1.0503 | 1.0525 | 2025-01-07 13:00 | 2025-12-31 21:00
4241 | [6 empty] | 310 | 310 | 287 | 0 | High | 1.06 | 1.05 | 1.0506 | 2025-01-01 09:00 | 2025-12-31 02:00
4379 | 539S_13.8_G113.800 |  | 25 | FORT MCM | 25 | Northeast | 289 | 289 | 272 | 0 | High | 1.0518 | 1.05 | 1.0505 | 2025-01-07 10:00 | 2025-12-09 08:00
25295 | [6 empty] | 280 | 280 | 269 | 0 | High | 1.053 | 1.05 | 1.0511 | 2025-01-01 03:00 | 2025-12-16 17:00
3038 | [6 empty] | 277 | 277 | 277 | 0 | High | 1.0537 | 1.0501 | 1.0524 | 2025-01-01 | 2025-12-26 17:00
4222 | [6 empty] | 273 | 273 | 270 | 0 | High | 1.052 | 1.05 | 1.051 | 2025-01-07 09:00 | 2025-12-29 17:00
3194 | LAKE LA9 | 25 |  |  |  |  | 269 | 269 | 263 | 0 | High | 1.0629 | 1.05 | 1.0524 | 2025-01-07 23:00 | 2025-12-31 05:00
4194 | LAKE LO9 | 25 |  |  |  |  | 259 | 259 | 256 | 0 | High | 1.0627 | 1.05 | 1.0523 | 2025-01-07 23:00 | 2025-12-31 05:00
557 | [6 empty] | 250 | 250 | 248 | 0 | High | 1.0533 | 1.05 | 1.0517 | 2025-01-07 23:00 | 2025-12-31 05:00
533 | VICTORIA | 69 |  |  |  |  | 249 | 249 | 246 | 0 | High | 1.0541 | 1.05 | 1.0512 | 2025-01-07 10:00 | 2025-11-15 06:00
554 | [6 empty] | 242 | 242 | 240 | 0 | High | 1.0532 | 1.05 | 1.0517 | 2025-01-07 23:00 | 2025-12-31 05:00
3058 | [6 empty] | 234 | 234 | 221 | 0 | High | 1.0537 | 1.05 | 1.0509 | 2025-01-01 03:00 | 2025-12-16 17:00
4211 | [6 empty] | 232 | 232 | 229 | 0 | High | 1.0565 | 1.05 | 1.0512 | 2025-01-07 23:00 | 2025-12-31 05:00
3295 | [6 empty] | 218 | 218 | 214 | 0 | High | 1.0712 | 1.05 | 1.0529 | 2025-01-07 23:00 | 2025-12-31 05:00
4169 | [6 empty] | 217 | 217 | 213 | 0 | High | 1.053 | 1.05 | 1.051 | 2025-01-07 23:00 | 2025-12-31 05:00
3169 | [6 empty] | 210 | 210 | 208 | 0 | High | 1.0538 | 1.05 | 1.0514 | 2025-01-08 06:00 | 2025-12-31 05:00
4177 | [6 empty] | 196 | 196 | 195 | 0 | High | 1.0588 | 1.05 | 1.0523 | 2025-01-07 23:00 | 2025-12-31 02:00
944 | 638S TAP | 69 |  |  |  |  | 196 | 196 | 165 | 0 | High | 1.0511 | 1.05 | 1.0503 | 2025-01-02 08:00 | 2025-12-22 18:00
18070 | CRANBER8 | 15 |  |  |  |  | 196 | 196 | 0 | 185 | Low | 0.95 | 0.9483 | 0.94951 | 2025-01-07 11:00 | 2025-12-09 08:00
4295 | [6 empty] | 167 | 167 | 164 | 0 | High | 1.0684 | 1.05 | 1.0546 | 2025-01-07 11:00 | 2025-12-29 18:00
337 | ESSO JU8 | 69 |  |  |  |  | 163 | 163 | 144 | 0 | High | 1.051 | 1.05 | 1.0503 | 2025-01-02 08:00 | 2025-12-22 18:00
375 | [6 empty] | 160 | 160 | 0 | 156 | Low | 0.95 | 0.8854 | 0.94687 | 2025-01-07 13:00 | 2025-12-31 20:00
3170 | [6 empty] | 157 | 157 | 155 | 0 | High | 1.0716 | 1.05 | 1.0545 | 2025-01-08 06:00 | 2025-12-31 21:00
4949 | [6 empty] | 157 | 157 | 150 | 0 | High | 1.0711 | 1.05 | 1.0523 | 2025-01-09 04:00 | 2025-12-31 05:00
502 | [6 empty] | 154 | 154 | 151 | 0 | High | 1.0564 | 1.05 | 1.0511 | 2025-01-07 10:00 | 2025-10-05 18:00
3067 | [6 empty] | 151 | 151 | 146 | 0 | High | 1.052 | 1.05 | 1.0508 | 2025-01-07 10:00 | 2025-01-28 10:00
4237 | [6 empty] | 151 | 151 | 140 | 0 | High | 1.0519 | 1.05 | 1.0508 | 2025-01-01 09:00 | 2025-12-26 08:00
19442 | BIG VAL9 | 25 |  |  |  |  | 148 | 148 | 148 | 0 | High | 1.0542 | 1.0501 | 1.0528 | 2025-01-07 22:00 | 2025-12-29 19:00
4312 | [6 empty] | 143 | 143 | 141 | 0 | High | 1.0539 | 1.05 | 1.0511 | 2025-01-07 13:00 | 2025-12-31 06:00
4170 | [6 empty] | 141 | 141 | 137 | 0 | High | 1.0718 | 1.05 | 1.0542 | 2025-01-07 13:00 | 2025-12-31 21:00
3312 | [6 empty] | 137 | 137 | 135 | 0 | High | 1.0544 | 1.05 | 1.0513 | 2025-01-07 13:00 | 2025-12-31 21:00
535 | GARNEAU8 | 69 |  |  |  |  | 133 | 133 | 129 | 0 | High | 1.0531 | 1.05 | 1.0508 | 2025-01-07 11:00 | 2025-01-28 10:00
4048 | DIAM SH9 | 13.8 |  |  |  |  | 133 | 133 | 126 | 0 | High | 1.0529 | 1.05 | 1.0507 | 2025-01-07 11:00 | 2025-01-27 21:00
4275 | [6 empty] | 126 | 126 | 123 | 0 | High | 1.052 | 1.05 | 1.0509 | 2025-01-01 09:00 | 2025-12-22 08:00
3286 | [6 empty] | 121 | 121 | 114 | 0 | High | 1.052 | 1.05 | 1.0506 | 2025-01-01 10:00 | 2025-12-18 16:00
4067 | [6 empty] | 113 | 113 | 105 | 0 | High | 1.0518 | 1.05 | 1.0507 | 2025-01-07 11:00 | 2025-01-27 21:00
4121 | [6 empty] | 111 | 111 | 109 | 0 | High | 1.0542 | 1.05 | 1.0514 | 2025-01-07 23:00 | 2025-12-31 21:00
3091 | NISKU A9 | 25 |  |  |  |  | 111 | 111 | 105 | 0 | High | 1.0528 | 1.05 | 1.0507 | 2025-01-07 10:00 | 2025-10-05 18:00
376 | [6 empty] | 99 | 99 | 0 | 94 | Low | 0.95 | 0.8862 | 0.94634 | 2025-01-07 13:00 | 2025-12-28 19:00
560003 | [6 empty] | 98 | 98 | 0 | 94 | Low | 0.95 | 0.9418 | 0.94798 | 2025-01-01 09:00 | 2025-12-25 16:00
561003 | [6 empty] | 98 | 98 | 0 | 94 | Low | 0.95 | 0.9418 | 0.94798 | 2025-01-01 09:00 | 2025-12-25 16:00
3275 | [6 empty] | 96 | 96 | 94 | 0 | High | 1.0562 | 1.05 | 1.0509 | 2025-01-01 09:00 | 2025-12-26 08:00
15351 | 942SD4 | 25 |  |  |  |  | 95 | 95 | 52 | 0 | High | 1.0503 | 1.05 | 1.0501 | 2025-01-07 11:00 | 2025-01-27 18:00
4051 | [6 empty] | 90 | 90 | 89 | 0 | High | 1.054 | 1.05 | 1.0521 | 2025-01-01 07:00 | 2025-12-13 08:00
557448 | [6 empty] | 90 | 90 | 49 | 0 | High | 1.0501 | 1.05 | 1.0501 | 2025-01-01 16:00 | 2025-12-27 04:00
19289 | [6 empty] | 84 | 84 | 50 | 0 | High | 1.0505 | 1.05 | 1.0501 | 2025-01-04 17:00 | 2025-12-26 18:00
4723 | BILBY 2 | 4.16 |  |  |  |  | 76 | 76 | 67 | 0 | High | 1.0524 | 1.05 | 1.0505 | 2025-01-08 16:00 | 2025-10-08 20:00
19439 | [6 empty] | 75 | 75 | 75 | 0 | High | 1.0518 | 1.0501 | 1.0508 | 2025-01-28 10:00 | 2025-11-15 15:00
4091 | NISKU 9 | 25 |  |  |  |  | 74 | 74 | 68 | 0 | High | 1.0524 | 1.05 | 1.0506 | 2025-01-07 10:00 | 2025-01-28 10:00
25296 | [6 empty] | 74 | 74 | 70 | 0 | High | 1.0523 | 1.05 | 1.0507 | 2025-01-07 17:00 | 2025-01-27 07:00
4081 | [6 empty] | 71 | 71 | 67 | 0 | High | 1.0519 | 1.05 | 1.0508 | 2025-01-01 01:00 | 2025-01-31 15:00
4038 | [6 empty] | 65 | 65 | 63 | 0 | High | 1.052 | 1.05 | 1.051 | 2025-01-01 07:00 | 2025-12-13 05:00
4005 | [6 empty] | 60 | 60 | 45 | 0 | High | 1.0511 | 1.05 | 1.0502 | 2025-01-07 18:00 | 2025-10-08 20:00
188 | [6 empty] | 50 | 50 | 47 | 0 | High | 1.0688 | 1.05 | 1.0557 | 2025-01-09 04:00 | 2025-12-28 19:00
3401 | [6 empty] | 49 | 49 | 48 | 0 | High | 1.0539 | 1.05 | 1.0515 | 2025-01-01 16:00 | 2025-12-26 08:00
4238 | [6 empty] | 47 | 47 | 47 | 0 | High | 1.0666 | 1.0517 | 1.0604 | 2025-01-09 04:00 | 2025-12-28 19:00
1357 | VILNA 7 | 138 |  |  |  |  | 45 | 45 | 41 | 0 | High | 1.051 | 1.05 | 1.0503 | 2025-01-07 16:00 | 2025-10-08 20:00
4444 | [6 empty] | 43 | 43 | 43 | 0 | High | 1.0743 | 1.0541 | 1.0658 | 2025-01-09 04:00 | 2025-12-28 19:00
3949 | [6 empty] | 43 | 43 | 43 | 0 | High | 1.067 | 1.0556 | 1.0646 | 2025-01-09 04:00 | 2025-12-28 19:00
4178 | [6 empty] | 42 | 42 | 42 | 0 | High | 1.0716 | 1.0506 | 1.06 | 2025-01-09 04:00 | 2025-12-28 19:00
4401 | [6 empty] | 42 | 42 | 41 | 0 | High | 1.0519 | 1.05 | 1.051 | 2025-01-01 09:00 | 2025-12-22 08:00
410 | WHITEGE8 | 69 |  |  |  |  | 42 | 42 | 29 | 0 | High | 1.0506 | 1.05 | 1.0501 | 2025-01-02 09:00 | 2025-12-22 17:00
4239 | [6 empty] | 41 | 41 | 41 | 0 | High | 1.0668 | 1.0526 | 1.0621 | 2025-01-09 04:00 | 2025-12-28 19:00
4183 | [6 empty] | 41 | 41 | 41 | 0 | High | 1.0561 | 1.0561 | 1.0561 | 2025-01-09 04:00 | 2025-12-28 19:00
3211 | [6 empty] | 41 | 41 | 34 | 0 | High | 1.0526 | 1.05 | 1.0504 | 2025-01-07 23:00 | 2025-12-29 20:00
4318 | [6 empty] | 40 | 40 | 38 | 0 | High | 1.0572 | 1.05 | 1.0547 | 2025-01-09 04:00 | 2025-12-28 19:00
4122 | [6 empty] | 37 | 37 | 35 | 0 | High | 1.0508 | 1.05 | 1.0504 | 2025-01-24 15:00 | 2025-11-26 13:00
4104 | [6 empty] | 36 | 36 | 36 | 0 | High | 1.0561 | 1.0501 | 1.0533 | 2025-01-09 04:00 | 2025-12-28 19:00
18274 | MACKAY2 18.000 |  | 25 | FORT MCM | 25 | Northeast | 35 | 35 | 29 | 0 | High | 1.0532 | 1.05 | 1.051 | 2025-05-29 09:00 | 2025-12-09 08:00
3340 | [6 empty] | 30 | 30 | 29 | 0 | High | 1.0527 | 1.05 | 1.0512 | 2025-01-09 23:00 | 2025-12-28 19:00
4111 | [6 empty] | 24 | 24 | 22 | 0 | High | 1.0514 | 1.05 | 1.0504 | 2025-01-01 16:00 | 2025-12-25 16:00
3355 | [6 empty] | 23 | 23 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-01-07 16:00 | 2025-12-18 11:00
19433 | [6 empty] | 20 | 20 | 19 | 0 | High | 1.0519 | 1.05 | 1.0508 | 2025-01-09 04:00 | 2025-12-28 19:00
552433 | [6 empty] | 20 | 20 | 19 | 0 | High | 1.0519 | 1.05 | 1.0508 | 2025-01-09 04:00 | 2025-12-28 19:00
4780 | [6 empty] | 20 | 20 | 20 | 0 | High | 1.0515 | 1.0501 | 1.0507 | 2025-01-09 23:00 | 2025-12-28 19:00
3302 | [6 empty] | 19 | 19 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-01-20 09:00 | 2025-12-28 19:00
3354 | [6 empty] | 19 | 19 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-01-16 15:00 | 2025-12-04 22:00
449 | [6 empty] | 17 | 17 | 17 | 0 | High | 1.0628 | 1.0524 | 1.0584 | 2025-04-09 09:00 | 2025-12-23 08:00
3301 | [6 empty] | 17 | 17 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-02-19 10:00 | 2025-12-31 21:00
3449 | [6 empty] | 16 | 16 | 16 | 0 | High | 1.0602 | 1.053 | 1.0562 | 2025-04-09 09:00 | 2025-12-23 08:00
4224 | [6 empty] | 16 | 16 | 16 | 0 | High | 1.0602 | 1.053 | 1.0562 | 2025-04-09 09:00 | 2025-12-23 08:00
539 | [6 empty] | 16 | 16 | 15 | 0 | High | 1.0515 | 1.05 | 1.0507 | 2025-01-07 19:00 | 2025-01-11 23:00
2780 | [6 empty] | 16 | 16 | 16 | 0 | High | 1.0514 | 1.0501 | 1.0506 | 2025-01-23 06:00 | 2025-12-28 19:00
4304 | PLAMOND9 | 25 |  |  |  |  | 15 | 15 | 11 | 0 | High | 1.0505 | 1.05 | 1.0502 | 2025-01-07 18:00 | 2025-01-09 17:00
4388 | ELLIS2 9 | 13.8 |  |  |  |  | 14 | 14 | 7 | 0 | High | 1.0504 | 1.05 | 1.0501 | 2025-01-08 16:00 | 2025-12-22 16:00
2405 | CONKLIN2 13.800 |  | 25 | FORT MCM | 25 | Northeast | 14 | 14 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-02-23 | 2025-12-31 06:00
4097 | [6 empty] | 12 | 12 | 11 | 0 | High | 1.0577 | 1.05 | 1.0537 | 2025-01-12 09:00 | 2025-12-19 03:00
4257 | [6 empty] | 12 | 12 | 12 | 0 | High | 1.0562 | 1.054 | 1.0553 | 2025-01-09 04:00 | 2025-12-19 03:00
4243 | [6 empty] | 10 | 10 | 10 | 0 | High | 1.0575 | 1.0503 | 1.0536 | 2025-02-13 15:00 | 2025-12-23 08:00
4254 | [6 empty] | 9 | 9 | 9 | 0 | High | 1.0514 | 1.0501 | 1.0509 | 2025-01-09 04:00 | 2025-06-21 21:00
447 | [6 empty] | 9 | 9 | 9 | 0 | High | 1.0513 | 1.0503 | 1.0506 | 2025-01-12 08:00 | 2025-12-10 16:00
3447 | [6 empty] | 9 | 9 | 9 | 0 | High | 1.0513 | 1.0503 | 1.0506 | 2025-01-12 08:00 | 2025-12-10 16:00
4245 | [6 empty] | 9 | 9 | 9 | 0 | High | 1.0513 | 1.0503 | 1.0506 | 2025-01-12 08:00 | 2025-12-10 16:00
2239 | [6 empty] | 8 | 8 | 8 | 0 | High | 1.0581 | 1.0505 | 1.055 | 2025-02-13 15:00 | 2025-12-23 08:00
4107 | SUNDRE 9 | 25 |  |  |  |  | 8 | 8 | 7 | 0 | High | 1.0505 | 1.05 | 1.0502 | 2025-01-11 15:00 | 2025-12-23 16:00
3556 | [6 empty] | 7 | 7 | 7 | 0 | High | 1.0528 | 1.0505 | 1.0515 | 2025-01-09 04:00 | 2025-12-19 03:00
18433 | [6 empty] | 6 | 6 | 6 | 0 | High | 1.0515 | 1.0501 | 1.0506 | 2025-02-13 15:00 | 2025-11-17 23:00
229 | [6 empty] | 6 | 6 | 0 | 6 | Low | 0.9499 | 0.8852 | 0.9341 | 2025-04-09 09:00 | 2025-09-04 15:00
236 | [6 empty] | 5 | 5 | 5 | 0 | High | 1.0521 | 1.0503 | 1.051 | 2025-03-20 | 2025-11-23 04:00
4276 | [6 empty] | 5 | 5 | 5 | 0 | High | 1.0509 | 1.0501 | 1.0505 | 2025-01-02 09:00 | 2025-04-10 02:00
19142 | BEARCK3 13.800 |  | 20 | GRANDE P | 20 | Northwest | 5 | 5 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-03-02 15:00 | 2025-12-02 10:00
71003 | [6 empty] | 5 | 5 | 0 | 4 | Low | 0.95 | 0.9425 | 0.94692 | 2025-04-09 09:00 | 2025-12-10 05:00
71004 | [6 empty] | 5 | 5 | 0 | 4 | Low | 0.95 | 0.9425 | 0.94692 | 2025-04-09 09:00 | 2025-12-10 05:00
25323 | [6 empty] | 5 | 5 | 0 | 5 | Low | 0.9499 | 0.9493 | 0.94964 | 2025-01-31 23:00 | 2025-06-12 22:00
329 | [6 empty] | 5 | 5 | 0 | 5 | Low | 0.9427 | 0.8985 | 0.93348 | 2025-04-09 09:00 | 2025-09-04 15:00
2218 | [6 empty] | 4 | 4 | 4 | 0 | High | 1.0506 | 1.0501 | 1.0503 | 2025-01-08 16:00 | 2025-01-09 17:00
377 | [6 empty] | 4 | 4 | 0 | 4 | Low | 0.9476 | 0.9049 | 0.93675 | 2025-04-09 09:00 | 2025-09-04 15:00
2231 | [6 empty] | 3 | 3 | 2 | 0 | High | 1.0568 | 1.05 | 1.0524 | 2025-04-11 10:00 | 2025-07-05 16:00
553447 | [6 empty] | 3 | 3 | 2 | 0 | High | 1.0531 | 1.05 | 1.0519 | 2025-01-12 08:00 | 2025-07-24 22:00
2344 | [6 empty] | 3 | 3 | 1 | 0 | High | 1.0502 | 1.05 | 1.0501 | 2025-03-11 06:00 | 2025-12-25 16:00
3020 | [6 empty] | 3 | 3 | 2 | 0 | High | 1.0501 | 1.05 | 1.0501 | 2025-01-02 08:00 | 2025-01-06 16:00
4232 | [6 empty] | 3 | 3 | 0 | 3 | Low | 0.9371 | 0.8861 | 0.91717 | 2025-06-12 22:00 | 2025-09-04 15:00
18448 | [6 empty] | 2 | 2 | 2 | 0 | High | 1.0523 | 1.0517 | 1.052 | 2025-06-12 22:00 | 2025-07-24 22:00
554448 | [6 empty] | 2 | 2 | 2 | 0 | High | 1.0523 | 1.0517 | 1.052 | 2025-06-12 22:00 | 2025-07-24 22:00
19423 | [6 empty] | 2 | 2 | 1 | 0 | High | 1.0517 | 1.05 | 1.0509 | 2025-02-18 07:00 | 2025-07-24 22:00
3218 | [6 empty] | 2 | 2 | 2 | 0 | High | 1.0505 | 1.0502 | 1.0503 | 2025-01-08 16:00 | 2025-01-09 17:00
3331 | [6 empty] | 2 | 2 | 1 | 0 | High | 1.0502 | 1.05 | 1.0501 | 2025-01-02 08:00 | 2025-02-13 15:00
4445 | [6 empty] | 2 | 2 | 2 | 0 | High | 1.0502 | 1.0502 | 1.0502 | 2025-01-02 09:00 | 2025-01-12 08:00
710 | [6 empty] | 2 | 2 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-02-07 23:00 | 2025-12-26 06:00
19448 | [6 empty] | 2 | 2 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-02-19 02:00 | 2025-12-06 20:00
2402 | [6 empty] | 2 | 2 | 0 | 2 | Low | 0.9471 | 0.9431 | 0.9451 | 2025-06-12 22:00 | 2025-07-24 22:00
3402 | [6 empty] | 2 | 2 | 0 | 2 | Low | 0.9464 | 0.9425 | 0.94445 | 2025-06-12 22:00 | 2025-07-24 22:00
161 | [6 empty] | 1 | 1 | 1 | 0 | High | 1.0535 | 1.0535 | 1.0535 | 2025-07-24 22:00 | 2025-07-24 22:00
2005 | [6 empty] | 1 | 1 | 1 | 0 | High | 1.0533 | 1.0533 | 1.0533 | 2025-12-10 05:00 | 2025-12-10 05:00
4042 | [6 empty] | 1 | 1 | 1 | 0 | High | 1.0527 | 1.0527 | 1.0527 | 2025-02-13 15:00 | 2025-02-13 15:00
4101 | [6 empty] | 1 | 1 | 1 | 0 | High | 1.0509 | 1.0509 | 1.0509 | 2025-02-13 15:00 | 2025-02-13 15:00
4090 | [6 empty] | 1 | 1 | 1 | 0 | High | 1.0503 | 1.0503 | 1.0503 | 2025-01-08 16:00 | 2025-01-08 16:00
18223 | TAR-GN-2 13.800 |  | 25 | FORT MCM | 25 | Northeast | 1 | 1 | 0 | 0 | High | 1.05 | 1.05 | 1.05 | 2025-11-18 13:00 | 2025-11-18 13:00
17163 | [6 empty] | 1 | 1 | 0 | 1 | Low | 0.9498 | 0.9498 | 0.9498 | 2025-02-04 19:00 | 2025-02-04 19:00
4264 | [6 empty] | 1 | 1 | 0 | 1 | Low | 0.9483 | 0.9483 | 0.9483 | 2025-06-12 22:00 | 2025-06-12 22:00
2234 | [6 empty] | 1 | 1 | 0 | 1 | Low | 0.9473 | 0.9473 | 0.9473 | 2025-09-04 15:00 | 2025-09-04 15:00
3234 | [6 empty] | 1 | 1 | 0 | 1 | Low | 0.9428 | 0.9428 | 0.9428 | 2025-09-04 15:00 | 2025-09-04 15:00

## System_Summary
N-0 System Summary
Metric | Value | Unit
Solved / analyzed hours |  | hours
Maximum pre-ACCOR loading |  | %
Average of hourly maximum loading |  | %
Maximum simultaneous thermal violations |  | count
Average simultaneous thermal violations |  | count
Maximum simultaneous voltage violations |  | count
Average simultaneous voltage violations |  | count
Number of violated branches |  | branches
Number of violating buses |  | buses
Monthly Stress Pattern
month | hours_analyzed | max_loading_pre | avg_max_loading_pre | avg_thermal_viol_pre | max_thermal_viol_pre | avg_voltage_viol_pre | max_voltage_viol_pre
2025-01 | 623 | 162.25 | 129.8726 | 4.1027 | 8 | 550.1445 | 587
2025-02 | 549 | 158.47 | 135.4722 | 4.4827 | 8 | 531.7596 | 561
2025-03 | 559 | 158.71 | 135.6114 | 4.0215 | 8 | 536.6601 | 563
2025-04 | 210 | 165.01 | 148.023 | 4.8857 | 8 | 533.181 | 562
2025-05 | 47 | 161.78 | 149.4145 | 5.3404 | 7 | 524.383 | 545
2025-06 | 125 | 161.49 | 145.1442 | 4.544 | 8 | 535.224 | 559
2025-07 | 360 | 162.52 | 139.7491 | 4.3639 | 8 | 536.8611 | 563
2025-08 | 397 | 160.86 | 141.096 | 4.4962 | 7 | 529.8715 | 566
2025-09 | 551 | 161.59 | 136.2777 | 4.1488 | 9 | 537.4791 | 570
2025-10 | 660 | 161.13 | 134.6078 | 3.9682 | 7 | 540.2212 | 581
2025-11 | 598 | 161.02 | 136.3928 | 4.3712 | 9 | 539.4281 | 573
2025-12 | 536 | 161.93 | 135.2045 | 4.5131 | 9 | 538.3078 | 569

## Thermal_Results
N-0 Thermal Congestion Results
Ranking is based on violated hours for persistence and on peak loading for maximum overload. Both rankings are computed from the pre-ACCOR N-0 thermal violation scan.
Top 10 Congested Lines by Violation Frequency | [7 empty] | Top 10 Congested Lines by Maximum Overload
Rank | Branch | Circuits | Violated hours | Share of solved hours (%) | Maximum loading (%) | Average loading (%) | Total excess above 100 (%) | Rank | Branch | Circuits | Violated hours | Share of solved hours (%) | Maximum loading (%) | Average loading (%) | Total excess above 100 (%)
1 | 816-817 | 87 | 5128 | 98.3317 | 165.01 | 136.3184 | 186240.78 | 1 | 816-817 | 87 | 5128 | 98.3317 | 165.01 | 136.3184 | 186240.78
2 | 817-818 | 87 | 4710 | 90.3164 | 150.72 | 123.0652 | 108637.03 | 2 | 817-818 | 87 | 4710 | 90.3164 | 150.72 | 123.0652 | 108637.03
3 | 12-412 | 20 | 4117 | 78.9453 | 128.89 | 113.9978 | 57628.93 | 3 | 31-272 | 10 | 1323 | 25.3691 | 142.6 | 117.561 | 23233.14
4 | 818-819 | 87 | 3617 | 69.3576 | 139.97 | 114.6918 | 53140.22 | 4 | 818-819 | 87 | 3617 | 69.3576 | 139.97 | 114.6918 | 53140.22
5 | 816-1501 | 87 | 1436 | 27.536 | 111.85 | 103.6894 | 5298.01 | 5 | 329-819 | 87 | 789 | 15.1294 | 133.55 | 104.5148 | 3562.15
6 | 31-272 | 10 | 1323 | 25.3691 | 142.6 | 117.561 | 23233.14 | 6 | 12-412 | 20 | 4117 | 78.9453 | 128.89 | 113.9978 | 57628.93
7 | 20-88 | 40 | 921 | 17.6606 | 107.07 | 102.3774 | 2189.57 | 7 | 4120-558120 | F1 | 40 | 0.76702 | 125.72 | 100.7802 | 31.21
8 | 329-819 | 87 | 789 | 15.1294 | 133.55 | 104.5148 | 3562.15 | 8 | 159-480 | 14 | 3 | 0.057526 | 122.34 | 107.8633 | 23.59
9 | 873-875 | 79 | 240 | 4.6021 | 102.15 | 101.8269 | 438.45 | 9 | 456-90000 | 01 | 6 | 0.11505 | 119.68 | 105.5483 | 33.29
10 | 20-39 | 02 | 72 | 1.3806 | 103.07 | 101.2261 | 88.28 | 10 | 816-1501 | 87 | 1436 | 27.536 | 111.85 | 103.6894 | 5298.01
Thermal Interpretation Notes
• The most persistent bottleneck is 816-817, which is overloaded in 5128 out of 5215 solved hours.
• The highest single-hour thermal stress in the system is 165.01% on branch 816-817.
• The top-10 tables are the clearest line-level results for the written N-0 report; the full all-line ranking is kept in a separate workbook.

## Voltage_Results
N-0 Voltage Results
The ranking below emphasizes persistence first, then severity. In this dataset, the dominant behaviour is high-voltage violation rather than low-voltage violation.
Rank | Bus | Bus name | kV | Area | Region | Hours violated | Dominant type | Max pu | Min pu | Average pu | Severity margin (pu) | Voltage Interpretation Notes
1 | 10605 | THICKWD | 23 |  |  | 5215 | High | 1.2691 | 1.2414 | 1.2592 | 0.2191 | • The top buses are ranked by hours violated; ties are broken using larger voltage deviation from planning limits.
2 | 3270 |  |  |  |  | 5215 | High | 1.2654 | 1.2533 | 1.2598 | 0.2154 | • The most severe high-voltage bus in the ranked set is bus 10605 (THICKWD).
3 | 1080 | WESLY C4 | 240 |  |  | 5215 | High | 1.131 | 1.1228 | 1.1282 | 0.081 | • Only a small number of persistent low-voltage cases appear in the current pre-ACCOR N-0 scan; most flagged buses are over-voltage cases.
4 | 1655 | DAWES240 | 240 |  |  | 5215 | High | 1.1239 | 1.1209 | 1.1221 | 0.0739 | • Area/region labels are included where they could be reliably mapped from the supporting project data.
5 | 1605 |  |  |  |  | 5215 | High | 1.12 | 1.12 | 1.12 | 0.07
6 | 1090 | MEIKLE1 | 138 |  |  | 5215 | High | 1.1176 | 1.1123 | 1.1154 | 0.0676
7 | 204 | MCMILLA4 | 240 |  |  | 5215 | High | 1.1174 | 1.1119 | 1.1143 | 0.0674
8 | 1050 | HOTCHKS7 | 138 |  |  | 5215 | High | 1.1173 | 1.112 | 1.1152 | 0.0673
9 | 1083 | CARMON 7 | 138 |  |  | 5215 | High | 1.1168 | 1.108 | 1.114 | 0.0668
10 | 1280 | BRINT02 | 240 |  |  | 5215 | High | 1.1165 | 1.1021 | 1.11 | 0.0665

## Critical_Hours_Top50
Top 50 Worst N-0 Hours for Selected N-1 Screening
These hours are ranked by maximum pre-ACCOR loading, then by number of thermal violations, then by total excess loading above 100%.
Rank | Hour | Month | Day | Max thermal loading (%) | Thermal violations | Voltage violations | Worst violating branch | Worst branch ckt | Total excess above 100 (%) | Violated branches
1 | 2025-04-11 10:00 | 2025-04 | Friday | 165.01 | 8 | 533 | 816-817 | 87 | 215.26 | 8
2 | 2025-04-09 09:00 | 2025-04 | Wednesday | 163.74 | 7 | 532 | 816-817 | 87 | 186 | 7
3 | 2025-07-26 20:00 | 2025-07 | Saturday | 162.52 | 8 | 546 | 816-817 | 87 | 189.81 | 8
4 | 2025-01-27 06:00 | 2025-01 | Monday | 162.25 | 6 | 561 | 816-817 | 87 | 192.53 | 6
5 | 2025-01-09 04:00 | 2025-01 | Thursday | 161.94 | 7 | 567 | 816-817 | 87 | 208.72 | 7
6 | 2025-12-19 03:00 | 2025-12 | Friday | 161.93 | 8 | 551 | 816-817 | 87 | 215.65 | 8
7 | 2025-04-25 02:00 | 2025-04 | Friday | 161.87 | 6 | 540 | 816-817 | 87 | 189.93 | 6
8 | 2025-05-07 23:00 | 2025-05 | Wednesday | 161.78 | 6 | 526 | 816-817 | 87 | 192.91 | 6
9 | 2025-01-09 23:00 | 2025-01 | Thursday | 161.59 | 7 | 574 | 816-817 | 87 | 204.58 | 7
10 | 2025-09-21 20:00 | 2025-09 | Sunday | 161.59 | 7 | 546 | 816-817 | 87 | 197.97 | 7
11 | 2025-06-21 21:00 | 2025-06 | Saturday | 161.49 | 7 | 552 | 816-817 | 87 | 203.14 | 7
12 | 2025-09-04 12:00 | 2025-09 | Thursday | 161.47 | 7 | 542 | 816-817 | 87 | 176.91 | 7
13 | 2025-12-05 01:00 | 2025-12 | Friday | 161.42 | 7 | 554 | 816-817 | 87 | 187.15 | 7
14 | 2025-04-26 02:00 | 2025-04 | Saturday | 161.35 | 7 | 545 | 816-817 | 87 | 185.77 | 7
15 | 2025-01-23 06:00 | 2025-01 | Thursday | 161.34 | 6 | 568 | 816-817 | 87 | 179.65 | 6
16 | 2025-12-19 04:00 | 2025-12 | Friday | 161.31 | 8 | 548 | 816-817 | 87 | 212.61 | 8
17 | 2025-04-10 02:00 | 2025-04 | Thursday | 161.25 | 6 | 551 | 816-817 | 87 | 195.15 | 6
18 | 2025-04-07 20:00 | 2025-04 | Monday | 161.19 | 7 | 553 | 816-817 | 87 | 194.15 | 7
19 | 2025-10-17 03:00 | 2025-10 | Friday | 161.13 | 6 | 552 | 816-817 | 87 | 182.61 | 6
20 | 2025-04-24 22:00 | 2025-04 | Thursday | 161.13 | 5 | 537 | 816-817 | 87 | 161.91 | 5
21 | 2025-07-07 22:00 | 2025-07 | Monday | 161.12 | 6 | 549 | 816-817 | 87 | 168.05 | 6
22 | 2025-09-06 01:00 | 2025-09 | Saturday | 161.05 | 7 | 554 | 816-817 | 87 | 172.73 | 7
23 | 2025-12-10 05:00 | 2025-12 | Wednesday | 161.03 | 7 | 559 | 816-817 | 87 | 175.27 | 7
24 | 2025-11-06 | 2025-11 | Thursday | 161.02 | 6 | 552 | 816-817 | 87 | 174.05 | 6
25 | 2025-08-25 01:00 | 2025-08 | Monday | 160.86 | 7 | 542 | 816-817 | 87 | 189.53 | 7
26 | 2025-12-10 03:00 | 2025-12 | Wednesday | 160.85 | 7 | 555 | 816-817 | 87 | 183.87 | 7
27 | 2025-10-08 | 2025-10 | Wednesday | 160.81 | 7 | 557 | 816-817 | 87 | 180.83 | 7
28 | 2025-12-15 19:00 | 2025-12 | Monday | 160.65 | 7 | 554 | 816-817 | 87 | 175.16 | 7
29 | 2025-09-17 21:00 | 2025-09 | Wednesday | 160.65 | 6 | 546 | 816-817 | 87 | 181.41 | 6
30 | 2025-12-28 19:00 | 2025-12 | Sunday | 160.51 | 6 | 555 | 816-817 | 87 | 180.96 | 6
31 | 2025-06-12 22:00 | 2025-06 | Thursday | 160.48 | 6 | 529 | 816-817 | 87 | 165.38 | 6
32 | 2025-06-07 22:00 | 2025-06 | Saturday | 160.16 | 6 | 555 | 816-817 | 87 | 172.41 | 6
33 | 2025-07-03 23:00 | 2025-07 | Thursday | 160.02 | 6 | 554 | 816-817 | 87 | 166.48 | 6
34 | 2025-07-24 22:00 | 2025-07 | Thursday | 160 | 7 | 552 | 816-817 | 87 | 196.22 | 7
35 | 2025-09-04 15:00 | 2025-09 | Thursday | 159.98 | 9 | 535 | 816-817 | 87 | 239.91 | 9
36 | 2025-06-19 21:00 | 2025-06 | Thursday | 159.84 | 6 | 538 | 816-817 | 87 | 159.37 | 6
37 | 2025-11-17 23:00 | 2025-11 | Monday | 159.75 | 6 | 551 | 816-817 | 87 | 166.49 | 6
38 | 2025-06-28 01:00 | 2025-06 | Saturday | 159.74 | 8 | 559 | 816-817 | 87 | 195.18 | 8
39 | 2025-10-19 03:00 | 2025-10 | Sunday | 159.62 | 6 | 541 | 816-817 | 87 | 181.68 | 6
40 | 2025-06-19 01:00 | 2025-06 | Thursday | 159.62 | 5 | 542 | 816-817 | 87 | 156 | 5
41 | 2025-01-26 21:00 | 2025-01 | Sunday | 159.6 | 6 | 553 | 816-817 | 87 | 175.27 | 6
42 | 2025-06-07 21:00 | 2025-06 | Saturday | 159.6 | 6 | 552 | 816-817 | 87 | 159 | 6
43 | 2025-01-10 02:00 | 2025-01 | Friday | 159.57 | 7 | 557 | 816-817 | 87 | 195.71 | 7
44 | 2025-07-11 03:00 | 2025-07 | Friday | 159.46 | 5 | 548 | 816-817 | 87 | 155.58 | 5
45 | 2025-10-11 05:00 | 2025-10 | Saturday | 159.26 | 5 | 555 | 816-817 | 87 | 154.93 | 5
46 | 2025-12-10 06:00 | 2025-12 | Wednesday | 159.21 | 6 | 550 | 816-817 | 87 | 164.85 | 6
47 | 2025-10-19 02:00 | 2025-10 | Sunday | 159.08 | 7 | 548 | 816-817 | 87 | 181.93 | 7
48 | 2025-12-04 22:00 | 2025-12 | Thursday | 159.07 | 8 | 535 | 816-817 | 87 | 193.58 | 8
49 | 2025-10-07 23:00 | 2025-10 | Tuesday | 158.98 | 7 | 536 | 816-817 | 87 | 177.81 | 7
50 | 2025-11-02 22:00 | 2025-11 | Sunday | 158.92 | 7 | 552 | 816-817 | 87 | 184.64 | 7

## Area_Context
Mapped Area Context (Supporting Only)
This sheet is included only as supporting context. Area mapping was available for a limited subset of violating buses, so line ranking and hour selection are based on direct branch/hour results instead.
Area number | Area name | Planning area | Region | Mapped buses with violations | Total violation events | Average hours violated | Worst max pu | Worst min pu
25 | FORT MCM | 25 | Northeast | 6 | 6159 | 1026.5 | 1.057 | 1.05
20 | GRANDE P | 20 | Northwest | 3 | 5807 | 1935.6667 | 1.0683 | 1.05
19 | PEACE RI | 19 | Northwest | 1 | 5215 | 5215 | 1.0774 | 1.0725
Visible-Sheet Source Map
Sheet | Data basis
System_Summary | Derived from n0_summary(1).csv
Thermal_Results | Derived from thermal_violations_pre_accor(1).csv
Voltage_Results | Derived from voltage_violations_pre_accor(1).csv and prior mapped bus report
Critical_Hours_Top50 | Derived from n0_summary(1).csv + thermal_violations_pre_accor(1).csv